## Sheet1
| DEFECT | [16 empty] | Plan |  |  | RECTIFY |  |  |  | RESCAN |  |  | PROGRESS |  | REMARKS | KPI
No | Report Date | Report By | Defect From | TEV/US In DB | Hotspot ∆T In ⁰C | Equipment | Switchgear Type | Switchgear Brand | Transformer Brand | Cable Type | Functional Location | Substation Name | Feeder No | Defect Description 1 | Defect Description 2 | Defect Description 3 ( FREE TEXT) | Criticality | Defect Owner | Repair Proposal | Target Date | Rectification Done Date | Parts | Action Taken 1 | Action Taken ( FREE TEXT ) | Rescan Date | Rescan Result | Remarks | Case Status | Report Deligated | If Repetitive Fault | OPF | REPAIR MEAN TIME
1 | 2023-01-16 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00728 | BKT CHERAS NO. 5 | OUTGOING 6 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-27 | 2023-01-27 | 2023-01-27 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-30 | CLEAR |  | CASE CLOSED |  |  |  | 11 | TRUE
2 | 2023-01-16 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00728 | BKT CHERAS NO. 5 | OUTGOING 6 | HOTSPOT | FUSE / LINK | BLUE PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-27 | 2023-01-27 | 2023-01-27 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-30 | CLEAR |  | CASE CLOSED |  |  |  | 11 | TRUE
3 | 2023-01-16 | KUASATEK PROTECTION | THERMOGRAPHY |  | 37 | LVDB / F.PILLAR |  |  |  | PILC | WKLS/PCE/J00729 | BKT CHERAS NO. 6 | OUTGOING 1 | HOTSPOT | FUSE / LINK | LVDB - OUTGOING F1 RED PHASE INCOMING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-17 | 2023-02-17 | 2023-02-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 32 | TRUE
4 | 2023-01-16 | KUASATEK PROTECTION | THERMOGRAPHY |  | 27 | LVDB / F.PILLAR |  |  |  | PILC | WKLS/PCE/J00729 | BKT CHERAS NO. 6 | OUTGOING 3 | HOTSPOT | FUSE / LINK | LVDB - OUTGOING F3 BLUE PHASE OUTGOING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-17 | 2023-02-17 | 2023-02-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 32 | TRUE
5 | 2023-01-16 | KUASATEK PROTECTION | THERMOGRAPHY |  | 29 | LVDB / F.PILLAR |  |  |  | PILC | WKLS/PCE/J00729 | BKT CHERAS NO. 6 | OUTGOING 5 | HOTSPOT | FUSE / LINK | LVDB - OUTGOING F5 BLUE PHASE OUTGOING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-17 | 2023-02-17 | 2023-02-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 32 | TRUE
6 | 2023-01-16 | KUASATEK PROTECTION | THERMOGRAPHY |  | 40 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00731 | BKT CHERAS NO. 8 | OUTGOING 4 | HOTSPOT | FUSE / LINK | RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-27 | 2023-01-27 | 2023-01-27 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-30 | CLEAR |  | CASE CLOSED |  |  |  | 11 | TRUE
7 | 2023-01-16 | KUASATEK PROTECTION | THERMOGRAPHY |  | 31 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00731 | BKT CHERAS NO. 8 | OUTGOING 4 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-27 | 2023-01-27 | 2023-01-27 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-30 | CLEAR |  | CASE CLOSED |  |  |  | 11 | TRUE
8 | 2023-01-16 | KUASATEK PROTECTION | THERMOGRAPHY |  | 1 | SWITCHGEAR | RMU MOTORIZED | F&G INDKOM |  |  | WKLS/PCE/J00739 | TMN ANGGERIK NO. 1 | TX PANEL | HOTSPOT | CABLE COMPARTMENT |  | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-02-22 | 2023-02-22 | RMU | TIGHTNESS INSPECTION | [8 empty] | 37 | TRUE
9 | 2023-01-16 | KUASATEK PROTECTION | THERMOGRAPHY |  | 30 | LVDB / F.PILLAR |  |  |  |  | WKLS/PCE/J00739 | TMN ANGGERIK NO. 1 | OTHERS | HOTSPOT | CURRENT TRANSFORMER | BLUE PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-27 | 2023-01-27 | 2023-01-27 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-30 | CLEAR |  | CASE CLOSED |  |  |  | 11 | TRUE
10 | 2023-01-16 | KUASATEK PROTECTION | THERMOGRAPHY |  | 10 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00739 | TMN ANGGERIK NO. 1 | OUTGOING 1 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-27 | 2023-01-27 | 2023-01-27 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-30 | CLEAR |  | CASE CLOSED |  |  |  | 11 | FALSE
11 | 2023-01-17 | KUASATEK PROTECTION | THERMOGRAPHY |  | 47 | LVDB / F.PILLAR |  |  |  | PILC | WKLS/PCE/J00744 | TMN DESA CHERAS | OUTGOING 2 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-27 | 2023-01-27 | 2023-01-27 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-30 | CLEAR |  | CASE CLOSED |  |  |  | 10 | TRUE
12 | 2023-01-17 | KUASATEK PROTECTION | THERMOGRAPHY |  | 33 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00744 | TMN DESA CHERAS | OUTGOING 7 | HOTSPOT | FUSE / LINK | RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-27 | 2023-01-27 | 2023-01-27 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-30 | CLEAR |  | CASE CLOSED |  |  |  | 10 | TRUE
13 | 2023-01-17 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00871 | NO. 2 RMH/KEDAI 3TKT JLN 1/154D DESA CHE | OUTGOING 7 | HOTSPOT | FUSE / LINK | LVDB: BLUE PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-27 | 2023-01-27 | 2023-01-27 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-30 | CLEAR |  | CASE CLOSED |  |  |  | 10 | TRUE
14 | 2023-01-17 | KUASATEK PROTECTION | THERMOGRAPHY |  | 30 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00871 | NO. 2 RMH/KEDAI 3TKT JLN 1/154D DESA CHE | OUTGOING 7 | HOTSPOT | FUSE / LINK | F/P: BLUE PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-27 | 2023-01-27 | 2023-01-27 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-30 | CLEAR |  | CASE CLOSED |  |  |  | 10 | TRUE
15 | 2023-01-17 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00871 | NO. 2 RMH/KEDAI 3TKT JLN 1/154D DESA CHE | OUTGOING 8 | HOTSPOT | FUSE / LINK | F/P: RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-27 | 2023-01-27 | 2023-01-27 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-30 | CLEAR |  | CASE CLOSED |  |  |  | 10 | TRUE
16 | 2023-01-17 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00231 | JLN DAMAI PERDANA 3/2 BDR DAMAI PERDANA | OUTGOING 5 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-27 | 2023-01-27 | 2023-01-27 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-31 | CLEAR |  | CASE CLOSED |  |  |  | 10 | TRUE
17 | 2023-01-19 | KUASATEK PROTECTION | ULTRASOUND | 35 |  | SWITCHGEAR | RMU SF6 | TOSHIBA |  |  | WKLS/PCE/J01017 | CHERAS TOL NO. 1 | TX PANEL | TRACKING SOUND | CABLE COMPARTMENT | 9934 – TX 500KVA CABLE COMPARTMENT - RMU MOTORIZED | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-02-23 | 2023-02-23 | RMU | REPLACEMENT | TUKAR SUISGEAR RMU SF6 KE MRMU SF6 | [7 empty] | 35 | TRUE
18 | 2023-01-19 | KUASATEK PROTECTION | THERMOGRAPHY |  | 35 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J01017 | CHERAS TOL NO. 1 | OUTGOING 5 | HOTSPOT | FUSE / LINK | RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-28 | 2023-01-28 | 2023-01-28 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-31 | CLEAR |  | CASE CLOSED |  |  |  | 9 | TRUE
19 | 2023-01-19 | KUASATEK PROTECTION | THERMOGRAPHY |  | 47 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J01017 | CHERAS TOL NO. 1 | OUTGOING 5 | HOTSPOT | FUSE / LINK | BLUE PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-28 | 2023-01-28 | 2023-01-28 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-31 | CLEAR |  | CASE CLOSED |  |  |  | 9 | TRUE
20 | 2023-01-19 | KUASATEK PROTECTION | THERMOGRAPHY |  | 19 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J01056 | RMH PAM CHERAS BARU | OUTGOING 1 | HOTSPOT | FUSE / LINK | BLUE PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-31 | 2023-01-31 | 2023-01-31 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-31 | CLEAR |  | CASE CLOSED |  |  |  | 12 | TRUE
21 | 2023-01-19 | KUASATEK PROTECTION | THERMOGRAPHY |  | 45 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J01056 | RMH PAM CHERAS BARU | OUTGOING 3 | HOTSPOT | FUSE / LINK | RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-31 | 2023-01-31 | 2023-01-31 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-31 | CLEAR |  | CASE CLOSED |  |  |  | 12 | TRUE
22 | 2023-01-19 | KUASATEK PROTECTION | THERMOGRAPHY |  | 20 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J01060 | TMN BKT MEWAH NO. 1 | INCOMING 1 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-02-17 | 2023-02-17 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 29 | TRUE
23 | 2023-01-19 | KUASATEK PROTECTION | THERMOGRAPHY |  | 19 | LVDB / F.PILLAR |  |  |  | PILC | WKLS/PCE/J01060 | TMN BKT MEWAH NO. 1 | OUTGOING 4 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-31 | 2023-01-31 | 2023-01-31 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-31 | CLEAR |  | CASE CLOSED |  |  |  | 12 | TRUE
24 | 2023-01-19 | KUASATEK PROTECTION | THERMOGRAPHY |  | 22 | LVDB / F.PILLAR |  |  |  | PILC | WKLS/PCE/J01060 | TMN BKT MEWAH NO. 1 | OUTGOING 6 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-31 | 2023-01-31 | 2023-01-31 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-31 | CLEAR |  | CASE CLOSED |  |  |  | 12 | TRUE
25 | 2023-01-19 | KUASATEK PROTECTION | THERMOGRAPHY |  | 38 | LVDB / F.PILLAR |  |  |  | PILC | WKLS/PCE/J01060 | TMN BKT MEWAH NO. 1 | OUTGOING 6 | HOTSPOT | FUSE / LINK | BLUE PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-31 | 2023-01-31 | 2023-01-31 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-31 | CLEAR |  | CASE CLOSED |  |  |  | 12 | TRUE
26 | 2023-01-19 | KUASATEK PROTECTION | THERMOGRAPHY |  | 47 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J01060 | TMN BKT MEWAH NO. 1 | OUTGOING 8 | HOTSPOT | FUSE / LINK | BLUE PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-31 | 2023-01-31 | 2023-01-31 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-31 | CLEAR |  | CASE CLOSED |  |  |  | 12 | TRUE
27 | 2023-01-19 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J01025 | JLN SEKUCI TMN BKT MEWAH | OUTGOING 5 | HOTSPOT | FUSE / LINK | BLUE PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-01-31 | 2023-01-31 | 2023-01-31 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | 2023-10-31 | CLEAR |  | CASE CLOSED |  |  |  | 12 | TRUE
28 | 2023-01-26 | KUASATEK PROTECTION | ULTRASOUND | 6 |  | SWITCHGEAR | VCB | TAMCO |  |  | WKLS/PCE/J00695 | TMN MIDAH NO. 6 | 11KV CABLE FEEDER | TRACKING SOUND | CABLE COMPARTMENT | 40107 – P/E THE HOLMES CABLE COMPARTMENT (TRACKING SOUND) | REPAIR IMMEDIATELY | CABLE MAINTENANCE |  | 2023-03-30 | 2023-02-13 | TERMINATION | NEW TERMINATION | Details : Termination guna heat shrink dan ada colour tape. Suis gear Vcb Tamco, saiz kabel 240mmp .Buat termination baru. Kerja siap dan normalised | [7 empty] | 18 | TRUE
29 | 2023-01-27 | KUASATEK PROTECTION | THERMOGRAPHY |  | 35 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00713 | MPIK NO-1 | OUTGOING 4 | HOTSPOT | FUSE / LINK | LVDB - OUTGOING F4 RED PHASE OUTGOING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-16 | 2023-02-16 | 2023-02-16 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 20 | TRUE
30 | 2023-01-30 | KUASATEK PROTECTION | THERMOGRAPHY |  | 26 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00343 | KUCHAI JAYA NO. 1 | OUTGOING 5 | HOTSPOT | FUSE / LINK | F/P - OUTGOING F5 BLUE PHASE OUTGOING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-16 | 2023-02-16 | 2023-02-16 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 17 | TRUE
31 | 2023-01-30 | KUASATEK PROTECTION | THERMOGRAPHY |  | 24 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00448 | TMN PAGAR RUYONG | OUTGOING 8 | HOTSPOT | FUSE / LINK | LVDB - OUTGOING F8 RED PHASE INCOMING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-16 | 2023-02-16 | 2023-02-16 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 17 | TRUE
32 | 2023-01-30 | KUASATEK PROTECTION | THERMOGRAPHY |  | 12 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00448 | TMN PAGAR RUYONG | OUTGOING 7 | HOTSPOT | FUSE / LINK | LVDB - OUTGOING F7 RED PHASE INCOMING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-16 | 2023-02-16 | 2023-02-16 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 17 | TRUE
33 | 2023-01-31 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00317 | UNITED GARDEN NO. 2 | OUTGOING 7 | HOTSPOT | FUSE / LINK | OUTGOING F7 RED PHASE OUTGOING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-14 | 2023-02-14 | 2023-02-14 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 14 | TRUE
34 | 2023-01-31 | KUASATEK PROTECTION | THERMOGRAPHY |  | 19 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00305 | BUKIT INDAH JLN KLANG LAMA | OUTGOING 5 | HOTSPOT | FUSE / LINK | OUTGOING F5 RED PHASE OUTGOING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-06 | 2023-04-06 | 2023-04-06 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 65 | TRUE
35 | 2023-01-31 | KUASATEK PROTECTION | THERMOGRAPHY |  | 16 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00351 | HAPPY GARDEN NO. 5 | OUTGOING 6 | HOTSPOT | CABLE LUG / TERMINATION | OUTGOING F6 RED PHASE CABLE TERMINATION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-07 | 2023-04-07 | 2023-04-07 | LUG | REPLACEMENT | TUKAR LUG YANG BARU | [7 empty] | 66 | TRUE
36 | 2023-01-31 | KUASATEK PROTECTION | THERMOGRAPHY |  | 47 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00351 | HAPPY GARDEN NO. 5 | OUTGOING 8 | HOTSPOT | FUSE / LINK | OUTGOING F8 BLUE PHASE INCOMING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-14 | 2023-02-14 | 2023-02-14 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 14 | TRUE
37 | 2023-01-31 | KUASATEK PROTECTION | THERMOGRAPHY |  | 40 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00351 | HAPPY GARDEN NO. 5 | OUTGOING 5 | HOTSPOT | FUSE / LINK | OUTGOING F5 RED PHASE OUTGOING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-14 | 2023-02-14 | 2023-02-14 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 14 | TRUE
38 | 2023-01-31 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00351 | HAPPY GARDEN NO. 5 | OUTGOING 5 | HOTSPOT | FUSE / LINK | OUTGOING F5 YELLOW PHASE OUTGOING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-14 | 2023-02-14 | 2023-02-14 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 14 | TRUE
39 | 2023-01-31 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00307 | HAPPY GARDEN NO. 6 | OUTGOING 3 | HOTSPOT | FUSE / LINK | OUTGOING F3 RED PHASE OUTGOING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-14 | 2023-02-14 | 2023-02-14 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 14 | TRUE
40 | 2023-02-08 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | PILC | WKLS/PCE/J01083 | TMN SHAMELIN PERKASA NO. 3 | OUTGOING 2 | HOTSPOT | FUSE / LINK | LVDB TX1 - OUTGOING F2 YELLOW PHASE OUTGOING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-18 | 2023-02-18 | 2023-02-18 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 10 | TRUE
41 | 2023-02-08 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J01083 | TMN SHAMELIN PERKASA NO. 3 | INCOMING 2 | HOTSPOT | FUSE / LINK | LVDB TX2 - INCOMING F2 BLUE PHASE OUTGOING LINK CONNECTION | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-02-26 | 2023-02-26 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 18 | TRUE
42 | 2023-02-08 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J01084 | TMN SHAMELIN PERKASA NO. 4 | INCOMING 2 | HOTSPOT | FUSE / LINK | LVDB TX1 - INCOMING F2 RED PHASE INCOMING LINK CONNECTION | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-02-26 | 2023-02-26 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 18 | TRUE
43 | 2023-02-08 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J01084 | TMN SHAMELIN PERKASA NO. 4 | INCOMING 2 | HOTSPOT | FUSE / LINK | LVDB TX1 - INCOMING F2 BLUE PHASE INCOMING LINK CONNECTION | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-02-26 | 2023-02-26 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 18 | TRUE
44 | 2023-02-08 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J01085 | TMN SHAMELIN PERKASA NO. 6 | OUTGOING 1 | HOTSPOT | FUSE / LINK | LVDB TX1 - OUTGOING F1 RED PHASE OUTGOING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-18 | 2023-02-18 | 2023-02-18 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 10 | TRUE
45 | 2023-02-08 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J01085 | TMN SHAMELIN PERKASA NO. 6 | OUTGOING 1 | HOTSPOT | FUSE / LINK | LVDB TX1 - OUTGOING F1 BLUE PHASE OUTGOING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-18 | 2023-02-18 | 2023-02-18 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 10 | TRUE
46 | 2023-02-08 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J01085 | TMN SHAMELIN PERKASA NO. 6 | OUTGOING 6 | HOTSPOT | FUSE / LINK | LVDB TX2 - OUTGOING F6 RED PHASE OUTGOING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-18 | 2023-02-18 | 2023-02-18 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 10 | TRUE
47 | 2023-02-08 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J01092 | TMN SHAMELIN PERKASA NO. 14 | OUTGOING 4 | HOTSPOT | FUSE / LINK | F/P - OUTGOING F4 RED PHASE OUTGOING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-18 | 2023-02-18 | 2023-02-18 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 10 | TRUE
48 | 2023-02-09 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J01074 | RMH PANJANG PUDU ULU | OUTGOING 2 | HOTSPOT | FUSE / LINK | LVDB - OUTGOING F2 RED PHASE INCOMING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-18 | 2023-02-18 | 2023-02-18 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 9 | TRUE
49 | 2023-02-10 | KUASATEK PROTECTION | THERMOGRAPHY |  | 42 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00698 | CHERAS LOW COST NO. 2 | OUTGOING 1 | HOTSPOT | FUSE / LINK | F/P - OUTGOING F1 RED PHASE INCOMING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-18 | 2023-02-18 | 2023-02-18 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 8 | TRUE
50 | 2023-02-10 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00703 | CHERAS LOW COST NO. 8 | OUTGOING 3 | HOTSPOT | FUSE / LINK | LVDDB - OUTGOING F3 RED PHASE INCOMING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-18 | 2023-02-18 | 2023-02-18 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 8 | TRUE
51 | 2023-02-10 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00672 | TMN TENAGA | OUTGOING 6 | HOTSPOT | FUSE / LINK | LVDB - OUTGOING F6 YELLOW PHASE INCOMING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-16 | 2023-02-16 | 2023-02-16 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 6 | TRUE
52 | 2023-02-10 | KUASATEK PROTECTION | THERMOGRAPHY |  | 21 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00672 | TMN TENAGA | OUTGOING 6 | HOTSPOT | CABLE LUG / TERMINATION | LVDB - OUTGOING F6 YELLOW PHASE INCOMING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-12 | 2023-04-12 | 2023-04-12 | LUG | REPLACEMENT | TUKAR LUG YANG BARU | [7 empty] | 61 | TRUE
53 | 2023-02-10 | KUASATEK PROTECTION | THERMOGRAPHY |  | 23 | OTHERS |  |  |  | XLPE | WKLS/PCE/J00672 | TMN TENAGA | OTHERS | HOTSPOT | CABLE LUG / TERMINATION | LVDB - OUTGOING F6 YELLOW PHASE INCOMING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-12 | 2023-04-12 | 2023-04-12 | LUG | REPLACEMENT | TUKAR LUG YANG BARU | [7 empty] | 61 | TRUE
54 | 2023-02-13 | KUASATEK PROTECTION | THERMOGRAPHY |  | 17 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00372 | SRI PETALING ZON F | INCOMING 1 | HOTSPOT | FUSE / LINK | F/P - INCOMING F1 NEUTRAL PHASE OUTGOING LINK CONNECTION | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-02-22 | 2023-02-22 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 9 | TRUE
55 | 2023-02-13 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00363 | TMN SRI INDAH NO. 5 | OUTGOING 7 | HOTSPOT | FUSE / LINK | LVDB - OUTGOING F7 RED PHASE OUTGOING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-17 | 2023-02-17 | 2023-02-17 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 4 | TRUE
56 | 2023-02-15 | KUASATEK PROTECTION | ULTRASOUND | 18 |  | SWITCHGEAR | RMU SF6 | F&G INDKOM |  | XLPE | WKLS/PCE/J00292 | KG PASIR DALAM | 11KV CABLE FEEDER | TRACKING SOUND | CABLE COMPARTMENT | TX 500KVA CABLE COMPARTMENT (TRACKING SOUND) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-03-18 | 2023-03-18 | RMU | TIGHTNESS INSPECTION | [8 empty] | 31 | TRUE
57 | 2023-02-16 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00089 | JLN 1/116C NO. 1 KUCHAI ENT PARK | OUTGOING 3 | HOTSPOT | FUSE / LINK | LVDB TX1 - OUTGOING F3 YELLOW PHASE OUTGOING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-28 | 2023-02-28 | 2023-02-28 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 12 | TRUE
58 | 2023-02-16 | KUASATEK PROTECTION | THERMOGRAPHY |  | 16 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00086 | JLN 1/116C NO. 2 KUCHAI ENT PARK | OUTGOING 1 | HOTSPOT | CABLE LUG / TERMINATION | LVDB TX2 - OUTGOING F1 NEUTRAL PHASE CABLE LUG | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-15 | 2023-05-15 | 2023-05-15 | CABLE LUG / TERMINATION | REPLACEMENT | tukar cable lug | [7 empty] | 88 | TRUE
59 | 2023-02-16 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00087 | JLN 12/116B KUCHAI ENT PARK NO. 2 | OUTGOING 1 | HOTSPOT | FUSE / LINK | LVDB - OUTGOING F1 YELLOW PHASE OUTGOING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-02-28 | 2023-02-28 | 2023-02-28 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 12 | TRUE
60 | 2023-02-22 | KUASATEK PROTECTION | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR |  |  |  | PILC | WKLS/PCE/J00719 | TMN MULIA NO. 2 | OUTGOING 6 | HOTSPOT | CABLE LUG / TERMINATION | LVDB - OUTGOING F6 YELLOW PHASE CABLE TERMINATION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-12 | 2023-04-12 | 2023-04-12 | LUG | REPLACEMENT | TUKAR LUG YANG ABRU | [7 empty] | 49 | TRUE
61 | 2023-02-23 | KUASATEK PROTECTION | ULTRASOUND | 30 |  | SWITCHGEAR | RMU SF6 | F&G INDKOM |  | PILC | WKLS/PCE/J00667 | SRI MAS NO.1 | OTHERS | TRACKING SOUND | CABLE COMPARTMENT | 12905 – P/E CHERAS LOW COST NO.4 (CABLE COMPARTMENT) (TRACKING SOUND) | REPAIR IMMEDIATELY | CABLE MAINTENANCE |  | 2023-04-30 | 2023-03-21 | TERMINATION | NEW TERMINATION | Details : Termination twist dan ada kesan bakar pada pangkal termaination serta ketiga-tiga stud bushing longgar. Suis gear Rmu Indkom, saiz kabel 185mmp pilc. Lay dan tukar kabel 150mmp xlpe sebanyak 20m.Buat 1x term & 1x trans joint serta ketatkan stud bushing. Kerja siap dan normalised | [7 empty] | 26 | TRUE
62 | 2023-02-23 | KUASATEK PROTECTION | THERMOGRAPHY |  | 19 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00704 | CHERAS PASAR MODEN | INCOMING 1 | HOTSPOT | FUSE / LINK | LVDB - INCOMING F1 RED PHASE INCOMING LINK CONNECTION | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-03-21 | 2023-03-21 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 26 | TRUE
63 | 2023-02-24 | KUASATEK PROTECTION | THERMOGRAPHY |  | 24 | LVDB / F.PILLAR |  |  |  | XLPE | WKLS/PCE/J00699 | CHERAS LOW COST NO. 3 | OUTGOING 3 | HOTSPOT | CABLE LUG / TERMINATION | LVDB - OUTGOING F3 YELLOW PHASE CABLE LUG | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-20 | 2023-06-20 | 2023-06-20 | LUG | REPLACEMENT | [8 empty] | 116 | TRUE
64 | 2023-02-24 | KUASATEK PROTECTION | THERMOGRAPHY |  | 41 | LVDB / F.PILLAR |  |  |  | PILC | WKLS/PCE/J00699 | CHERAS LOW COST NO. 3 | OUTGOING 3 | HOTSPOT | FUSE / LINK | F/P - OUTGOING F3 YELLOW PHASE INCOMING FUSE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-06 | 2023-03-06 | 2023-03-06 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 10 | TRUE
65 | 2023-02-28 | AKYZ ENGINEERING | ULTRASOUND | 3 |  | SWITCHGEAR | RMU SF6 | MERLIN GERIN | MTM | XLPE | WKLS/PCE/J00431 | BKT DESA KONDO | 11KV CABLE FEEDER | CORONA DISCHARGE | CABLE COMPARTMENT | PANEL 12836 - BLUE PHASE CABLE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-04-06 | 2023-04-06 | TERMINATION | REPLACEMENT | KERJA PENUKARAN SUISGEAR RMU SF6 MERLIN GERIN KE SUISGEAR MRMU SF6 INDKOM 2+1 | [7 empty] | 37 | TRUE
66 | 2023-02-28 | AKYZ ENGINEERING | ULTRASOUND | 5 |  | SWITCHGEAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01247 | SEK KEB DESA PERDANA | 11KV CABLE FEEDER | ARCHING SOUND | CABLE COMPARTMENT | PANEL 42441 | REPAIR IMMEDIATELY | CABLE MAINTENANCE |  | 2023-04-30 | 2023-03-14 | TERMINATION | NEW TERMINATION | Detail :suis gear rmu indkom..saiz kabel 240mmp xlpe..term heat shrink..ada kesan moister pada bimetal..tindakan buang pasir dalam trenching riseup kabel dan buat term baru.tutup pasir simen semula.kerja siap dan normalised. | [7 empty] | 14 | TRUE
67 | 2023-03-01 | AKYZ ENGINEERING | THERMOGRAPHY |  | 50 | LVDB / F.PILLAR | RMU SF6 | OTHERS | MTM | PILC | WKLS/PCE/J00821 | BDR TAR NO. 1 | OUTGOING 4 | HOTSPOT | FUSE / LINK | RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-06 | 2023-03-06 | 2023-03-06 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 5 | TRUE
68 | 2023-03-01 | AKYZ ENGINEERING | THERMOGRAPHY |  | 28 | LVDB / F.PILLAR | RMU SF6 | OTHERS | MTM | PILC | WKLS/PCE/J00821 | BDR TAR NO. 1 | OUTGOING 8 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-06 | 2023-03-06 | 2023-03-06 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 5 | TRUE
69 | 2023-03-01 | AKYZ ENGINEERING | THERMOGRAPHY |  | 24 | LVDB / F.PILLAR | RMU SF6 | TOSHIBA | MTM | XLPE | WKLS/PCE/J00818 | BDR TAR KILANG NO. 1 | OUTGOING 2 | HOTSPOT | FUSE / LINK | NEUTRAL PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-06 | 2023-03-06 | 2023-03-06 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 5 | TRUE
70 | 2023-03-02 | AKYZ ENGINEERING | THERMOGRAPHY |  | 26 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00829 | TMN IND RINGAN DESA TASIK | OUTGOING 3 | HOTSPOT | FUSE / LINK | RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-10 | 2023-03-10 | 2023-03-10 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 8 | TRUE
71 | 2023-03-02 | AKYZ ENGINEERING | THERMOGRAPHY |  | 28 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00829 | TMN IND RINGAN DESA TASIK | OUTGOING 4 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-10 | 2023-03-10 | 2023-03-10 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 8 | TRUE
72 | 2023-03-02 | AKYZ ENGINEERING | THERMOGRAPHY |  | 15 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00829 | TMN IND RINGAN DESA TASIK | OUTGOING 7 | HOTSPOT | FUSE / LINK | RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-10 | 2023-03-10 | 2023-03-10 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 8 | TRUE
73 | 2023-03-02 | AKYZ ENGINEERING | THERMOGRAPHY |  | 11 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00829 | TMN IND RINGAN DESA TASIK | INCOMING 1 | HOTSPOT | FUSE / LINK | RED PHASE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-03-21 | 2023-03-21 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 19 | TRUE
74 | 2023-03-02 | AKYZ ENGINEERING | THERMOGRAPHY |  | 39 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00829 | TMN IND RINGAN DESA TASIK | OUTGOING 4 | HOTSPOT | CABLE LUG / TERMINATION | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-10 | 2023-05-10 | 2023-05-10 | LUG | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 69 | TRUE
75 | 2023-03-02 | AKYZ ENGINEERING | THERMOGRAPHY |  | 26 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00829 | TMN IND RINGAN DESA TASIK | OUTGOING 5 | HOTSPOT | CABLE LUG / TERMINATION | BLUE PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-10 | 2023-05-10 | 2023-05-10 | LUG | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 69 | TRUE
76 | 2023-03-03 | AKYZ ENGINEERING | ULTRASOUND | 13 |  | SWITCHGEAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00835 | DESA TASEK NO. 4 | 11KV CABLE FEEDER | ARCHING SOUND | CABLE COMPARTMENT | PANEL 13420 - TX2 | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-03-18 | 2023-03-18 | RMU | TIGHTNESS INSPECTION | [8 empty] | 15 | TRUE
77 | 2023-03-07 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J01117 | DATARAN DWITASEK NO. 4 BDR SRI PERMAISUR | OUTGOING 5 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-10 | 2023-03-10 | 2023-03-10 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 3 | TRUE
78 | 2023-03-09 | AKYZ ENGINEERING | THERMOGRAPHY |  | 16 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00415 | LRG JUGRA | OUTGOING 5 | HOTSPOT | FUSE / LINK | RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-20 | 2023-03-20 | 2023-03-20 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 11 | TRUE
79 | 2023-03-09 | AKYZ ENGINEERING | THERMOGRAPHY |  | 17 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00415 | LRG JUGRA | OUTGOING 5 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-20 | 2023-03-20 | 2023-03-20 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 11 | TRUE
80 | 2023-03-09 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | EPE | MTM | XLPE | WKLS/PCE/J00426 | TMN DESA NO. 5 | OUTGOING 6 | HOTSPOT | FUSE / LINK | RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-22 | 2023-03-22 | 2023-03-22 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 13 | TRUE
81 | 2023-03-09 | AKYZ ENGINEERING | THERMOGRAPHY |  | 30 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00590 | DESA COMMERCIAL NO. 2 | OUTGOING 4 | HOTSPOT | FUSE / LINK | RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-21 | 2023-03-21 | 2023-03-21 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 12 | TRUE
82 | 2023-03-09 | AKYZ ENGINEERING | THERMOGRAPHY |  | 10 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00590 | DESA COMMERCIAL NO. 2 | OUTGOING 4 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-21 | 2023-03-21 | 2023-03-21 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 12 | TRUE
83 | 2023-03-10 | AKYZ ENGINEERING | ULTRASOUND | 21 |  | SWITCHGEAR | VCB | ITEM | MTM | XLPE | WKLS/PCE/J00135 | DANAU DESA COMMERCIAL | 11KV CABLE FEEDER | TRACKING SOUND | CABLE COMPARTMENT | PANEL 16266 - TX1 | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-03-31 | 2023-03-31 | TERMINATION | CLEANING | [8 empty] | 21 | TRUE
84 | 2023-03-10 | AKYZ ENGINEERING | THERMOGRAPHY |  | 18 | TRANSFORMER | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01266 | RUMAH GURU LORONG SEPUTEH KL | TX1 | HOTSPOT | TX CABLE | LV SIDE - BLUE PHASE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-04-15 | 2023-04-15 | CABLE END TO END | REPLACEMENT | [8 empty] | 36 | TRUE
85 | 2023-03-11 | AKYZ ENGINEERING | ULTRASOUND | 4 |  | TRANSFORMER | VCB | ITEM | SGB |  | WKLS/PCE/J00547 | BLK A P/PURI VISTA AMANI | TX1 | CORONA DISCHARGE | TX CABLE | BLUE PHASE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-04-13 | 2023-04-13 | TERMINATION | REPLACEMENT | [8 empty] | 33 | TRUE
86 | 2023-03-12 | AKYZ ENGINEERING | ULTRASOUND | 22 |  | SWITCHGEAR | VCB | UNIVAC | MTM | XLPE | WKLS/PCE/J00892 | BLK A P/PURI SRI PENARA BDR SRI PERMAISU | 11KV CABLE FEEDER | TRACKING SOUND | CABLE COMPARTMENT | PANEL 30407 - TX2 | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-05-29 | 2023-05-29 | BREAKER | REPLACEMENT | TUKAR S/GEAR VCB UNIVAC KE S/GEAR VCB TOSHIBA DAN CABLE HT TX | [7 empty] | 78
87 | 2023-03-12 | AKYZ ENGINEERING | THERMOGRAPHY |  | 3 | TRANSFORMER | VCB | UNIVAC | MTM | XLPE | WKLS/PCE/J00892 | BLK A P/PURI SRI PENARA BDR SRI PERMAISU | TX1 | HOTSPOT | TX CABLE | YELLOW PHASE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-05-29 | 2023-05-29 | TERMINATION | REPLACEMENT | TUKAR S/GEAR VCB MAHKOTA KE S/GEAR VCB TOSHIBA DAN CABLE HT TX | [7 empty] | 78 | TRUE
88 | 2023-03-12 | AKYZ ENGINEERING | THERMOGRAPHY |  | 6 | TRANSFORMER | VCB | OTHERS | MTM | XLPE | WKLS/PCE/J00893 | BLK B P/PURI SRI PENARA BDR SRI PERMAISU | TX1 | HOTSPOT | TX CABLE | YELLOW PHASE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-05-29 | 2023-05-29 | TERMINATION | REPLACEMENT | TUKAR S/GEAR VCB MAHKOTA KE S/GEAR VCB TOSHIBA DAN CABLE HT TX | [7 empty] | 78 | TRUE
89 | 2023-03-13 | AKYZ ENGINEERING | THERMOGRAPHY |  | 31 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00908 | NO. 2 TMN SRI TANMING | OUTGOING 5 | HOTSPOT | CABLE LUG / TERMINATION | BLUE PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-27 | 2023-05-27 | 2023-05-27 | FUSE / LINK | REPLACEMENT | MENUKAR GANTI FIUS HOLDER BARU | [7 empty] | 75 | TRUE
90 | 2023-03-13 | AKYZ ENGINEERING | THERMOGRAPHY |  | 40 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00908 | NO. 2 TMN SRI TANMING | OUTGOING 6 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-22 | 2023-03-23 | 2023-03-23 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 10 | TRUE
91 | 2023-03-13 | AKYZ ENGINEERING | THERMOGRAPHY |  | 34 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00908 | NO. 2 TMN SRI TANMING | OUTGOING 6 | HOTSPOT | CABLE LUG / TERMINATION | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-27 | 2023-05-27 | 2023-05-27 | FUSE / LINK | REPLACEMENT | MENUKAR GANTI FIUS HOLDER BARU | [7 empty] | 75 | TRUE
92 | 2023-03-14 | AKYZ ENGINEERING | TEV | 33 |  | SWITCHGEAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01229 | TMN DAMAI IMPIAN 2 JLN DAMAI IMPIAN 2/8B | 11KV CABLE FEEDER | TEV | CABLE COMPARTMENT | PANEL 41695 - PE JLN DAMAI PERDANA 3/2 | REPAIR IMMEDIATELY | CABLE MAINTENANCE |  | 2023-04-03 | 2023-04-03 | TERMINATION | NEW TERMINATION | Details : Termination guna heat shrink, ada carbonised pada stopper bimetal dan stud bushing longgar(yellow & blue) . Suis gear Rmu Indkom, saiz kabel 150mmp xlpe. Buat termination baru. Kerja siap dan normalised | [7 empty] | 20 | TRUE
93 | 2023-03-15 | AKYZ ENGINEERING | THERMOGRAPHY |  | 33 | LVDB / F.PILLAR | VCB | ITEM | MTM | XLPE | WKLS/PCE/J00544 | JLN DAMAI RASA 18 ALAM DAMAI | INCOMING 1 | HOTSPOT | FUSE / LINK | RED PHASE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-03-30 | 2023-03-30 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 15 | TRUE
94 | 2023-03-16 | AKYZ ENGINEERING | ULTRASOUND | 4 |  | TRANSFORMER | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01243 | THE CORNER ALAM DAMAI | TX1 | CORONA DISCHARGE | TX CABLE | CABLE INSULATION | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-04-30 | 2023-04-30 | TERMINATION | CLEANING | [8 empty] | 45 | TRUE
95 | 2023-03-16 | AKYZ ENGINEERING | ULTRASOUND | 1 |  | SWITCHGEAR | RMU OIL | TAMCO | MTM | XLPE | WKLS/PCE/J00725 | BKT CHERAS NO. 1 | TX PANEL | CORONA DISCHARGE | CABLE COMPARTMENT | PANEL 9260 - TX | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-04-16 | 2023-04-16 | RMU | REPLACEMENT | tukar suisgear rmu oil ke mrmu sf6 item | [7 empty] | 31 | TRUE
96 | 2023-03-16 | AKYZ ENGINEERING | THERMOGRAPHY |  | 2 | SWITCHGEAR | RMU SF6 | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00756 | TMN CONNAUGHT NO. 1 | TX PANEL | HOTSPOT | CABLE COMPARTMENT | PANEL 4743 - TX | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-04-30 | 2023-04-30 | RMU | TIGHTNESS INSPECTION | [8 empty] | 45 | TRUE
97 | 2023-03-16 | AKYZ ENGINEERING | THERMOGRAPHY |  | 33 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00756 | TMN CONNAUGHT NO. 1 | OUTGOING 2 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-28 | 2023-03-28 | 2023-03-28 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 12 | TRUE
98 | 2023-03-16 | AKYZ ENGINEERING | THERMOGRAPHY |  | 24 | LVDB / F.PILLAR | VCB | ITEM | MTM | XLPE | WKLS/PCE/J00754 | TMN ORKID DESA | OUTGOING 3 | HOTSPOT | FUSE / LINK | RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-28 | 2023-03-28 | 2023-03-28 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 12 | TRUE
99 | 2023-03-16 | AKYZ ENGINEERING | THERMOGRAPHY |  | 24 | LVDB / F.PILLAR | VCB | ITEM | MTM | XLPE | WKLS/PCE/J00754 | TMN ORKID DESA | OUTGOING 8 | HOTSPOT | FUSE / LINK | RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-28 | 2023-03-28 | 2023-03-28 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 12 | TRUE
100 | 2023-03-16 | AKYZ ENGINEERING | THERMOGRAPHY |  | 27 | LVDB / F.PILLAR | VCB | ITEM | MTM | XLPE | WKLS/PCE/J00754 | TMN ORKID DESA | OUTGOING 8 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-28 | 2023-03-28 | 2023-03-28 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 12 | TRUE
101 | 2023-03-16 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | ITEM | MTM | XLPE | WKLS/PCE/J00754 | TMN ORKID DESA | OUTGOING 7 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-28 | 2023-03-28 | 2023-03-28 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 12 | TRUE
102 | 2023-03-17 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TOPRANK | LKH | XLPE | WKLS/PCE/J00753 | JLN 11 BKT ANGGERIK | OUTGOING 5 | HOTSPOT | CABLE LUG / TERMINATION | RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-27 | 2023-05-27 | 2023-05-27 | FUSE / LINK | REPLACEMENT | MENUKAR GANTI FIUS HOLDER BARU | [7 empty] | 71 | TRUE
103 | 2023-03-17 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | TOSHIBA | MTM | XLPE | WKLS/PCE/J00737 | TELEKOM TAMAN ANGGERIK | OUTGOING 8 | HOTSPOT | FUSE / LINK | RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-28 | 2023-03-28 | 2023-03-28 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 11 | TRUE
104 | 2023-03-18 | AKYZ ENGINEERING | THERMOGRAPHY |  | 22 | LVDB / F.PILLAR | RMU SF6 | TAMCO | LKH | XLPE | WKLS/PCE/J00134 | TMN TAYNTON VIEW | OUTGOING 3 | HOTSPOT | FUSE / LINK | RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-28 | 2023-03-28 | 2023-03-28 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 10 | TRUE
105 | 2023-03-18 | AKYZ ENGINEERING | THERMOGRAPHY |  | 20 | LVDB / F.PILLAR | RMU SF6 | TAMCO | SGB | XLPE | WKLS/PCE/J00134 | TMN TAYNTON VIEW | OUTGOING 6 | HOTSPOT | FUSE / LINK | RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-28 | 2023-03-28 | 2023-03-28 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 10 | TRUE
106 | 2023-03-19 | AKYZ ENGINEERING | THERMOGRAPHY |  | 32 | LVDB / F.PILLAR | VCB | EPE | MTM | XLPE | WKLS/PCE/J00763 | TMN MARIKH | OUTGOING 2 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-29 | 2023-03-29 | 2023-03-29 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 10 | TRUE
107 | 2023-03-19 | AKYZ ENGINEERING | THERMOGRAPHY |  | 33 | LVDB / F.PILLAR | VCB | EPE | MTM | XLPE | WKLS/PCE/J00763 | TMN MARIKH | OUTGOING 2 | HOTSPOT | FUSE / LINK | BLUE PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-29 | 2023-03-29 | 2023-03-29 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 10 | TRUE
108 | 2023-03-19 | AKYZ ENGINEERING | THERMOGRAPHY |  | 14 | LVDB / F.PILLAR | VCB | EPE | MTM | XLPE | WKLS/PCE/J00763 | TMN MARIKH | OUTGOING 3 | HOTSPOT | FUSE / LINK | BLUE PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-29 | 2023-03-29 | 2023-03-29 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 10 | TRUE
109 | 2023-03-19 | AKYZ ENGINEERING | THERMOGRAPHY |  | 34 | LVDB / F.PILLAR | VCB | EPE | MTM | XLPE | WKLS/PCE/J00766 | AWANAPURI TMN MUTIARA | OUTGOING 8 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-29 | 2023-03-29 | 2023-03-29 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 10 | TRUE
110 | 2023-03-21 | AKYZ ENGINEERING | THERMOGRAPHY |  | 41 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00761 | TMN SUET CHOW | OUTGOING 1 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-29 | 2023-03-29 | 2023-03-29 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 8 | TRUE
111 | 2023-03-21 | AKYZ ENGINEERING | THERMOGRAPHY |  | 41 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00761 | TMN SUET CHOW | OUTGOING 3 | HOTSPOT | FUSE / LINK | BLUE PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-29 | 2023-03-29 | 2023-03-29 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 8 | TRUE
112 | 2023-03-21 | AKYZ ENGINEERING | THERMOGRAPHY |  | 43 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00761 | TMN SUET CHOW | OUTGOING 8 | HOTSPOT | FUSE / LINK | BLUE PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-29 | 2023-03-29 | 2023-03-29 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 8 | TRUE
113 | 2023-03-22 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00768 | TMN BILLION | OUTGOING 6 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-29 | 2023-03-29 | 2023-03-29 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 7 | TRUE
114 | 2023-03-22 | AKYZ ENGINEERING | THERMOGRAPHY |  | 4 | BATTERY | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J01059 | SEK SRI BISTARI TMN SHAMELIN PERKASA | OTHERS | HOTSPOT | OTHERS | BATTERY BANK | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-04-30 | 2023-04-12 | OTHERS | TIGHTNESS INSPECTION | [8 empty] | 21 | TRUE
115 | 2023-03-22 | AKYZ ENGINEERING | ULTRASOUND |  | 12 | SWITCHGEAR | VCB | UNIVAC | MTM | XLPE | WKLS/PCE/J01058 | SEK KEB PANDAN PERDANA JLN PERDANA 3/1 | 11KV CABLE FEEDER | TRACKING SOUND | BREAKER COMPARTMENT | PANEL 30091 - TX | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-04-09 | 2023-04-09 | BREAKER | REPLACEMENT | TUKAR SUISGEAR VCB UNIVAC KE SUISGEAR VCB TAMCO | [7 empty] | 18 | TRUE
116 | 2023-03-23 | AKYZ ENGINEERING | THERMOGRAPHY |  | 22 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00705 | TMN MIHARJA NO. 1 | OUTGOING 8 | HOTSPOT | FUSE / LINK | RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-29 | 2023-03-29 | 2023-03-29 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 6 | TRUE
117 | 2023-03-23 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | ITEM | MTM | XLPE | WKLS/PCE/J01078 | TMN SEGAR NO. 3 | OUTGOING 7 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-29 | 2023-03-29 | 2023-03-29 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 6 | TRUE
118 | 2023-03-23 | AKYZ ENGINEERING | THERMOGRAPHY |  | 6 | TRANSFORMER | RMU SF6 | ITEM | MTM | XLPE | WKLS/PCE/J01078 | TMN SEGAR NO. 3 | TX1 | HOTSPOT | TX BUSHING | BLUE PHASE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-05-18 | 2023-05-18 | TX HV BUSHING | TIGHTNESS INSPECTION | [8 empty] | 56 | TRUE
119 | 2023-03-24 | AKYZ ENGINEERING | THERMOGRAPHY |  | 42 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00554 | VISTAMAS JLN PERSIARAN HARTAMAS | OUTGOING 4 | HOTSPOT | FUSE / LINK | BLUE PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-30 | 2023-03-30 | 2023-03-30 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 6 | TRUE
120 | 2023-03-25 | AKYZ ENGINEERING | THERMOGRAPHY |  | 4 | SWITCHGEAR | RMU SF6 | TAMCO | OTHERS | XLPE | WKLS/PCE/J01055 | RMH PAM BT 7 1/2 JLN CHERAS | 11KV CABLE FEEDER | HOTSPOT | CABLE COMPARTMENT | PANEL 19278 - SG MIDAH S/S | REPAIR IMMEDIATELY | CABLE MAINTENANCE |  | 2023-05-30 | 2023-04-11 | TERMINATION | NEW TERMINATION | Details : Termination ada kesan bakar pada red phase dan ada colour tape. Suis gear Rmu Falcon Beta, saiz kabel 185mmp pilc.Tukar short lenght kabel 150mmp xlpe sebanyak 25m. Buat 1xterm & 1 trans joint. Kerja siap dan normalised | [7 empty] | 17 | TRUE
121 | 2023-03-25 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | TAMCO | OTHERS | XLPE | WKLS/PCE/J01055 | RMH PAM BT 7 1/2 JLN CHERAS | OUTGOING 7 | HOTSPOT | FUSE / LINK | RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-30 | 2023-03-30 | 2023-03-30 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 5 | TRUE
122 | 2023-03-25 | AKYZ ENGINEERING | THERMOGRAPHY |  | 31 | LVDB / F.PILLAR | RMU SF6 | TAMCO | OTHERS | XLPE | WKLS/PCE/J01055 | RMH PAM BT 7 1/2 JLN CHERAS | OUTGOING 7 | HOTSPOT | FUSE / LINK | YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-03-30 | 2023-03-30 | 2023-03-30 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 5 | TRUE
123 | 2023-03-27 | AKYZ ENGINEERING | ULTRASOUND | 5 |  | SWITCHGEAR | VCB | TAMCO |  |  | WKLS/PCE/J01817 | SSU 11KV RESIDENSI TROFI 1 | 11KV CABLE FEEDER | ARCHING SOUND | CABLE COMPARTMENT | PANEL 56110 - PENGGUNA NO.4 | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-31 | 2023-07-31 | CABLE COMPARTMENT | TIGHTNESS INSPECTION | [8 empty] | 126 | TRUE
124 | 2023-03-27 | AKYZ ENGINEERING | ULTRASOUND | 28 |  | SWITCHGEAR | RMU SF6 | F&G INDKOM | SGB | XLPE | WKLS/PCE/J00708 | FLATTED FACTORY | 11KV CABLE FEEDER | TRACKING SOUND | CABLE COMPARTMENT | PANEL 6346 - SEK YUEN JLN 2 | REPAIR IMMEDIATELY | CABLE MAINTENANCE |  | 2023-05-30 | 2023-05-06 | TERMINATION | NEW TERMINATION | Details : Termination crossing dan ada colour tape. Suis gear Rmu Indkom, saiz kabel 185mmp pilc.Tukar short lenght kabel 150mmp xlpe sebanyak 20m. Buat 1xterm & 1 trans joint. Kerja siap dan normalised. (Hujan) | [7 empty] | 40 | TRUE
125 | 2023-03-29 | AKYZ ENGINEERING | ULTRASOUND | 3 |  | SWITCHGEAR | RMU SF6 | SIEMENS | OTHERS | XLPE | WKLS/PCE/J01592 | MASJID IBNU KHALDUN | 11KV CABLE FEEDER | CORONA DISCHARGE | CABLE COMPARTMENT | PANEL 51194 - PE POLIS QTRS | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-05-12 | 2023-05-12 | TERMINATION | CLEANING | [8 empty] | 44 | TRUE
126 | 2023-04-03 | AMT SOLUTIONS | ULTRASOUND | 2 |  | SWITCHGEAR | VCB | AICHI | MTM | PILC | WKLS/PCE/J00428 | TMN BKT DESA | TX PANEL | MECHANICAL VIBRATION | BUSBAR COMPARTMENT | BUSBAR COMP - TX (2dB) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-05-26 | 2023-05-26 | BUSBAR | REPLACEMENT | TUKAR S/GEAR VCB AICHI KE S/GEAR TOSHIBA SERTA TX CONSERV.TANK KE TX HERMATICALLY SEALED | [7 empty] | 53 | TRUE
127 | 2023-04-03 | AMT SOLUTIONS | THERMOGRAPHY |  | 41 | LVDB / F.PILLAR | VCB | AICHI | MTM | PILC | WKLS/PCE/J00428 | TMN BKT DESA | OUTGOING 1 | HOTSPOT | FUSE / LINK | OUTGOING 1 - YELLOW PHASE FUSE LINK (40.7 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-20 | 2023-04-20 | 2023-04-20 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 17 | TRUE
128 | 2023-04-03 | AMT SOLUTIONS | THERMOGRAPHY |  | 38 | LVDB / F.PILLAR | VCB | TAMCO | LKH | XLPE | WKLS/PCE/J00126 | RENONG WEST COURT | OUTGOING 3 | HOTSPOT | FUSE / LINK | OUTGOING 3 - YELLOW PHASE FUSE LINK (37.8 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-24 | 2023-04-24 | 2023-04-24 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 21 | TRUE
129 | 2023-04-03 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00857 | LUXURY FLAT | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING 6 - YELLOW PHASE FUSE LINK (189.7 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-22 | 2023-04-22 | 2023-04-22 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 19 | TRUE
130 | 2023-04-05 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | EPE | MTM | PILC | WKLS/PCE/J00141 | JLN DESA UTAMA | OUTGOING 4 | HOTSPOT | FUSE / LINK | OUTGOING 4 - BLUE PHASE FUSE LINK (56.6 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-20 | 2023-04-20 | 2023-04-20 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 15 | TRUE
131 | 2023-04-05 | AMT SOLUTIONS | THERMOGRAPHY |  | 49 | LVDB / F.PILLAR | VCB | EPE | MTM | PILC | WKLS/PCE/J00141 | JLN DESA UTAMA | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING 6 - RED PHASE FUSE LINK (48.7 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-20 | 2023-04-20 | 2023-04-20 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 15 | TRUE
132 | 2023-04-05 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | EPE | MTM | PILC | WKLS/PCE/J00141 | JLN DESA UTAMA | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING 6 - YELLOW PHASE FUSE LINK (231.5 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-20 | 2023-04-20 | 2023-04-20 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 15 | TRUE
133 | 2023-04-05 | AMT SOLUTIONS | THERMOGRAPHY |  | 43 | LVDB / F.PILLAR | VCB | EPE | MTM | PILC | WKLS/PCE/J00141 | JLN DESA UTAMA | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING 6 - BLUE PHASE FUSE LINK (43.0 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-20 | 2023-04-20 | 2023-04-20 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 15 | TRUE
134 | 2023-04-05 | AMT SOLUTIONS | THERMOGRAPHY |  | 34 | LVDB / F.PILLAR | VCB | EPE | MTM | PILC | WKLS/PCE/J00141 | JLN DESA UTAMA | OUTGOING 1 | HOTSPOT | FUSE / LINK | OUTGOING 1 - BLUE PHASE FUSE LINK (33.8 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-20 | 2023-04-20 | 2023-04-20 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 15 | TRUE
135 | 2023-04-05 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | EPE | MTM | PILC | WKLS/PCE/J00141 | JLN DESA UTAMA | OUTGOING 4 | HOTSPOT | FUSE / LINK | OUTGOING 4 - RED PHASE FUSE LINK (64.9 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-20 | 2023-04-20 | 2023-04-20 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 15 | TRUE
136 | 2023-04-05 | AMT SOLUTIONS | THERMOGRAPHY |  | 29 | LVDB / F.PILLAR | VCB | EPE | MTM | PILC | WKLS/PCE/J00141 | JLN DESA UTAMA | OUTGOING 7 | HOTSPOT | FUSE / LINK | OUTGOING 7 - BLUE PHASE FUSE LINK (28.6 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-20 | 2023-04-20 | 2023-04-20 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 15 | TRUE
137 | 2023-04-06 | AMT SOLUTIONS | THERMOGRAPHY |  | 2 | TRANSFORMER | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00430 | OBD TOWER | TX2 | HOTSPOT | TX CABLE | RED & YELLOW PHASE CABLE (1.7 °C) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-05-10 | 2023-05-10 | TERMINATION | REPLACEMENT | [8 empty] | 34 | TRUE
138 | 2023-04-06 | AMT SOLUTIONS | ULTRASOUND | 16 |  | SWITCHGEAR | VCB | TAMCO | MTM |  | WKLS/PCE/J00442 | PLAZA FABER | TX PANEL | MECHANICAL VIBRATION | PT COMPARTMENT | PT COMP - 11644 PENGGUNA (16dB) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-05-28 | 2023-05-28 | PT HOLDER | TIGHTNESS INSPECTION | [8 empty] | 52 | TRUE
139 | 2023-04-06 | AMT SOLUTIONS | THERMOGRAPHY |  | 1 | SWITCHGEAR | VCB | TAMCO | MTM |  | WKLS/PCE/J00442 | PLAZA FABER | TX PANEL | HOTSPOT | PT COMPARTMENT | PT COMP - 11644 PENGGUNA (1.3 °C) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-05-28 | 2023-05-28 | PT HOLDER | TIGHTNESS INSPECTION | [8 empty] | 52 | TRUE
140 | 2023-04-06 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00442 | PLAZA FABER | OUTGOING 1 | HOTSPOT | FUSE / LINK | OUTGOING 1 - RED PHASE FUSE LINK (131.1 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-23 | 2023-04-23 | 2023-04-23 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 17 | TRUE
141 | 2023-04-06 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00442 | PLAZA FABER | OUTGOING 1 | HOTSPOT | FUSE / LINK | OUTGOING 1 - YELLOW PHASE FUSE LINK (120.2 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-23 | 2023-04-23 | 2023-04-23 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 17 | TRUE
142 | 2023-04-06 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00427 | TMN DESA NO. 4 | OUTGOING 1 | HOTSPOT | FUSE / LINK | OUTGOING 1 - RED PHASE FUSE LINK (184.9 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-19 | 2023-04-19 | 2023-04-19 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 13 | TRUE
143 | 2023-04-06 | AMT SOLUTIONS | ULTRASOUND | 2 |  | SWITCHGEAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00136 | P/PURI DANAU PERMAI | 11KV CABLE FEEDER | CORONA DISCHARGE | BREAKER COMPARTMENT | BREAKER COMP - 16084 TAMAN DESA NO. 4 (2dB) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-05-16 | 2023-05-16 | BREAKER | SERVICING (CB ONLY) | [8 empty] | 40 | TRUE
144 | 2023-04-06 | AMT SOLUTIONS | THERMOGRAPHY |  | 2 | TRANSFORMER | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00136 | P/PURI DANAU PERMAI | TX2 | HOTSPOT | TX CABLE | YELLOW PHASE CABLE (2.7 °C) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-05-16 | 2023-05-16 | TERMINATION | REPLACEMENT | [8 empty] | 40 | TRUE
145 | 2023-04-07 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | SGB | XLPE | WKLS/PCE/J00122 | TMN DESA NO. 2 | OUTGOING 8 | HOTSPOT | FUSE / LINK | OUTGOING 8 - BLUE PHASE FUSE LINK (99.0 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-19 | 2023-04-19 | 2023-04-19 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 12 | TRUE
146 | 2023-04-10 | AMT SOLUTIONS | ULTRASOUND | 2 |  | SWITCHGEAR | VCB | ITEM | MTM |  | WKLS/PCE/J00137 | BLK A APT MEWAH ABADI INDAH JLN 2/109C | 11KV CABLE FEEDER | CORONA DISCHARGE | BREAKER COMPARTMENT | BREAKER COMP - 21039 PMU DANAU DESA CB 12 (2dB) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-05-18 | 2023-05-18 | BREAKER | SERVICING (CB ONLY) | [8 empty] | 38 | TRUE
147 | 2023-04-10 | AMT SOLUTIONS | THERMOGRAPHY |  | 39 | LVDB / F.PILLAR | RMU SF6 | ITEM | MTM | PILC | WKLS/PCE/J00447 | JLN DESA | OUTGOING 3 | HOTSPOT | FUSE / LINK | OUTGOING 3 - RED PHASE FUSE LINK (39.4 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-19 | 2023-04-19 | 2023-04-19 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 9 | TRUE
148 | 2023-04-10 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | ITEM | MTM | PILC | WKLS/PCE/J00447 | JLN DESA | OUTGOING 3 | HOTSPOT | FUSE / LINK | OUTGOING 3 - YELLOW PHASE FUSE LINK (51.5 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-19 | 2023-04-19 | 2023-04-19 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 9 | TRUE
149 | 2023-04-10 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | ITEM | MTM | PILC | WKLS/PCE/J00447 | JLN DESA | OUTGOING 3 | HOTSPOT | FUSE / LINK | OUTGOING 3 - BLUE PHASE FUSE LINK (107.7 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-19 | 2023-04-19 | 2023-04-19 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 9 | TRUE
150 | 2023-04-10 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | LKH HSS | MTM | XLPE | WKLS/PCE/J00439 | KUCHAI BUSINES CENTRE NO. 1 | OUTGOING 3 | HOTSPOT | FUSE / LINK | OUTGOING 3 - RED PHASE FUSE LINK (70.9 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-22 | 2023-04-22 | 2023-04-22 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 12 | TRUE
151 | 2023-04-10 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | LKH HSS | MTM | XLPE | WKLS/PCE/J00439 | KUCHAI BUSINES CENTRE NO. 1 | OUTGOING 3 | HOTSPOT | FUSE / LINK | OUTGOING 3 - BLUE PHASE FUSE LINK (71.6 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-22 | 2023-04-22 | 2023-04-22 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 12 | TRUE
152 | 2023-04-10 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | LKH HSS | MTM | XLPE | WKLS/PCE/J00439 | KUCHAI BUSINES CENTRE NO. 1 | OUTGOING 4 | HOTSPOT | FUSE / LINK | OUTGOING 4 - YELLOW PHASE FUSE LINK (154.5 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-22 | 2023-04-22 | 2023-04-22 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 12 | TRUE
153 | 2023-04-10 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | LKH HSS | MTM | XLPE | WKLS/PCE/J00439 | KUCHAI BUSINES CENTRE NO. 1 | OUTGOING 4 | HOTSPOT | FUSE / LINK | OUTGOING 4 - BLUE PHASE FUSE LINK (52.3 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-22 | 2023-04-22 | 2023-04-22 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 12 | TRUE
154 | 2023-04-12 | AMT SOLUTIONS | ULTRASOUND | 2 |  | SWITCHGEAR | VCB | ITEM | EWT | XLPE | WKLS/PCE/J00440 | FULL GOSPEL HALL | TX PANEL | CORONA DISCHARGE | BREAKER COMPARTMENT | BREAKER COMP - 4528 TX (2dB) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-06-05 | 2023-06-05 | BREAKER | NONE | TEAM CBM DAH RESCAN DAN TIADA DEFECT | [7 empty] | 54 | TRUE
155 | 2023-04-12 | AMT SOLUTIONS | THERMOGRAPHY |  | 48 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00303 | BDR PARK NO. 2 | OUTGOING 3 | HOTSPOT | FUSE / LINK | OUTGOING 3 - BLUE PHASE FUSE LINK (48.6 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-21 | 2023-04-21 | 2023-04-21 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 9 | TRUE
156 | 2023-04-12 | AMT SOLUTIONS | THERMOGRAPHY |  | 40 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00303 | BDR PARK NO. 2 | OUTGOING 7 | HOTSPOT | FUSE / LINK | OUTGOING 7 - BLUE PHASE FUSE LINK (39.7 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-21 | 2023-04-21 | 2023-04-21 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 9 | TRUE
157 | 2023-04-13 | AMT SOLUTIONS | THERMOGRAPHY |  | 36 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | PILC | WKLS/PCE/J00304 | BDR PARK NO. 1 | OUTGOING 2 | HOTSPOT | FUSE / LINK | OUTGOING 2 - RED PHASE FUSE LINK (36.2 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-21 | 2023-04-21 | 2023-04-21 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 8 | TRUE
158 | 2023-04-13 | AMT SOLUTIONS | THERMOGRAPHY |  | 39 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00304 | BDR PARK NO. 1 | OUTGOING 3 | HOTSPOT | FUSE / LINK | OUTGOING 3 - YELLOW PHASE FUSE LINK (39.6 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-21 | 2023-04-21 | 2023-04-21 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 8 | TRUE
159 | 2023-04-13 | AMT SOLUTIONS | ULTRASOUND | 7 |  | SWITCHGEAR | RMU SF6 | LUCY | MTM | XLPE | WKLS/PCE/J00316 | BAN LEE JLN KLANG LAMA | 11KV CABLE FEEDER | CORONA DISCHARGE | CABLE COMPARTMENT | CABLE COMP - 2263 RESIDENSI V (7dB) | REPAIR IMMEDIATELY | CABLE MAINTENANCE |  | 2023-06-30 | 2023-05-31 | TERMINATION | NEW TERMINATION | Details : Termination dalam keadaan baik. Suis gear Rmu Lucy, saiz kabel 150mmp xlpe. Buat termination baru. Kerja siap dan normalised. | [7 empty] | 48 | TRUE
160 | 2023-04-13 | AMT SOLUTIONS | THERMOGRAPHY |  | 2 | SWITCHGEAR | RMU SF6 | SIEMENS | MTM | XLPE | WKLS/PCE/J00300 | TMN TERTAMA | TX PANEL | HOTSPOT | OTHERS | FUSE COMP - 8819 TX1 (2.0 °C) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-06-11 | 2023-06-11 | RMU | TIGHTNESS INSPECTION | BUAT PREVENTIVE MAINTENANCE PADA SUISGEAR RMU SF6 SIEMENS | [7 empty] | 59 | TRUE
161 | 2023-04-13 | AMT SOLUTIONS | THERMOGRAPHY |  | 32 | LVDB / F.PILLAR | RMU SF6 | SIEMENS | MTM | PILC | WKLS/PCE/J00300 | TMN TERTAMA | OUTGOING 5 | HOTSPOT | FUSE / LINK | OUTGOING 5 - BLUE PHASE FUSE LINK (31.8 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-21 | 2023-04-21 | 2023-04-21 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 8 | TRUE
162 | 2023-04-13 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | SIEMENS | MTM | PILC | WKLS/PCE/J00300 | TMN TERTAMA | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING 6 - BLUE PHASE FUSE LINK (119.7 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-21 | 2023-04-21 | 2023-04-21 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 8 | TRUE
163 | 2023-04-13 | AMT SOLUTIONS | THERMOGRAPHY |  | 29 | LVDB / F.PILLAR | RMU SF6 | SIEMENS | MTM | XLPE | WKLS/PCE/J00300 | TMN TERTAMA | OUTGOING 1 | HOTSPOT | FUSE / LINK | OUTGOING 1 - RED PHASE FUSE LINK (29.0 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-21 | 2023-04-21 | 2023-04-21 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 8 | TRUE
164 | 2023-04-13 | AMT SOLUTIONS | ULTRASOUND | 3 |  | SWITCHGEAR | RMU MOTORIZED | F&G INDKOM | MTM |  | WKLS/PCE/J00302 | MEADOW PARK NO. 1 | 11KV CABLE FEEDER | CORONA DISCHARGE | CABLE COMPARTMENT | CABLE COMP - 10620 P/PURI CINDAIMAS (3dB) | REPAIR IMMEDIATELY | CABLE MAINTENANCE |  | 2023-06-30 | 2023-05-22 | TERMINATION | NEW TERMINATION | Details : Termination crossing, guna heat shrink dan stud bushing longgar(red dan blue) . Suis gear Rmu Indkom, saiz kabel 150mmp xlpe.Tukar termination cold shrink dan tukar bimetal, kabel pendek, laluan kabel bawah tong gas fire fighting(perlu alih untuk tukar short lenght) Kerja siap dan normalised. | [7 empty] | 39 | TRUE
165 | 2023-04-14 | AMT SOLUTIONS | THERMOGRAPHY |  | 26 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | PILC | WKLS/PCE/J00344 | HAPPY GARDEN NO. 2 | OUTGOING 5 | HOTSPOT | FUSE / LINK | OUTGOING 5 - BLUE PHASE FUSE LINK (25.7 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-20 | 2023-04-20 | 2023-04-20 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 6 | TRUE
166 | 2023-04-14 | AMT SOLUTIONS | THERMOGRAPHY |  | 33 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00093 | SRI DESA ENT PARK NO. 2 | INCOMING 1 | HOTSPOT | FUSE / LINK | INCOMING 1 - RED PHASE LINK (32.8 °C) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-05-02 | 2023-05-02 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 18 | TRUE
167 | 2023-04-15 | AMT SOLUTIONS | THERMOGRAPHY |  | 48 | LVDB / F.PILLAR | VCB | TAMCO | SGB | XLPE | WKLS/PCE/J00222 | PLAZA PRIMA | OUTGOING 4 | HOTSPOT | FUSE / LINK | OUTGOING 4 - RED PHASE FUSE LINK (48.3 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-21 | 2023-04-21 | 2023-04-21 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 6 | TRUE
168 | 2023-04-15 | AMT SOLUTIONS | THERMOGRAPHY |  | 41 | LVDB / F.PILLAR | VCB | TAMCO | SGB | XLPE | WKLS/PCE/J00222 | PLAZA PRIMA | OUTGOING 4 | HOTSPOT | FUSE / LINK | OUTGOING 4 - BLUE PHASE FUSE LINK (41.5 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-21 | 2023-04-21 | 2023-04-21 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 6 | TRUE
169 | 2023-04-15 | AMT SOLUTIONS | ULTRASOUND | 16 |  | SWITCHGEAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00280 | R/K PEJ 4 TKT JLN PUCHONG | TX PANEL | TRACKING SOUND | OTHERS | FUSE COMP - 29761 TX1 (16dB) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-05-03 | 2023-05-03 | RMU | TIGHTNESS INSPECTION | [8 empty] | 18 | TRUE
170 | 2023-04-15 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00280 | R/K PEJ 4 TKT JLN PUCHONG | OUTGOING 7 | HOTSPOT | FUSE / LINK | OUTGOING 7 - BLUE PHASE FUSE LINK (55.6 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-20 | 2023-04-20 | 2023-04-20 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 5 | TRUE
171 | 2023-04-15 | AMT SOLUTIONS | THERMOGRAPHY |  | 2 | TRANSFORMER | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00190 | KONDO SRI JATI 2 BLK B | TX2 | HOTSPOT | TX CABLE | CABLE SPLIT (2.2 °C) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-05-21 | 2023-05-21 | TERMINATION | REPLACEMENT | [8 empty] | 36 | TRUE
172 | 2023-04-16 | AMT SOLUTIONS | THERMOGRAPHY |  | 1 | SWITCHGEAR | RMU MOTORIZED | F&G INDKOM | MTM |  | WKLS/PCE/J00275 | TMN TAN YEW LAI NO.1 | 11KV CABLE FEEDER | HOTSPOT | CABLE COMPARTMENT | CABLE COMP - 1296 P/E RMH KEDAI/PEJABAT 4 TKT JLN PUCHONG (1.4 °C) | REPAIR IMMEDIATELY | CABLE MAINTENANCE |  | 2023-06-30 | 2023-05-24 | TERMINATION | NEW TERMINATION | Details : Termination twist dan 2 stud bushing longgar(yellow & blue) . Suis gear Rmu Indkom, saiz kabel 120mmp pilc.Tukar short lenght kabel 150mmp xlpe sebanyak 30m. Buat 1xterm & 1 trans joint. Kerja siap dan normalised. | [7 empty] | 38 | TRUE
173 | 2023-04-16 | AMT SOLUTIONS | THERMOGRAPHY |  | 23 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00275 | TMN TAN YEW LAI NO.1 | OUTGOING 8 | HOTSPOT | FUSE / LINK | OUTGOING 8 - BLUE PHASE FUSE LINK (23.1 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-21 | 2023-04-21 | 2023-04-21 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 5 | TRUE
174 | 2023-04-16 | AMT SOLUTIONS | THERMOGRAPHY |  | 30 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00275 | TMN TAN YEW LAI NO.1 | OUTGOING 9 | HOTSPOT | FUSE / LINK | OUTGOING 9 - BLUE PHASE FUSE LINK (30.6 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-21 | 2023-04-21 | 2023-04-21 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 5 | TRUE
175 | 2023-04-16 | AMT SOLUTIONS | THERMOGRAPHY |  | 25 | LVDB / F.PILLAR | VCB | GEC | MTM | PILC | WKLS/PCE/J00042 | TMN TAN YEW LAI NO. 3 | OUTGOING 7 | HOTSPOT | FUSE / LINK | OUTGOING 7 - YELLOW PHASE FUSE LINK (25.3 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-21 | 2023-04-21 | 2023-04-21 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 5 | TRUE
176 | 2023-04-16 | AMT SOLUTIONS | THERMOGRAPHY |  | 43 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00265 | TMN TAN YEW LAI NO. 2 | OUTGOING 4 | HOTSPOT | FUSE / LINK | OUTGOING 4 - RED PHASE FUSE LINK (43.8 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-21 | 2023-04-21 | 2023-04-21 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 5 | TRUE
177 | 2023-04-16 | AMT SOLUTIONS | THERMOGRAPHY |  | 22 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00265 | TMN TAN YEW LAI NO. 2 | OUTGOING 5 | HOTSPOT | FUSE / LINK | OUTGOING 5 - RED PHASE FUSE LINK (22.2 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-21 | 2023-04-21 | 2023-04-21 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 5 | TRUE
178 | 2023-04-16 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00265 | TMN TAN YEW LAI NO. 2 | OUTGOING 8 | HOTSPOT | FUSE / LINK | OUTGOING 8 - YELLOW PHASE FUSE LINK (69.8 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-04-21 | 2023-04-21 | 2023-04-21 | FUSE / LINK | REPLACEMENT | TUKAR GANTI YANG BARU | [7 empty] | 5 | TRUE
179 | 2023-04-17 | AMT SOLUTIONS | THERMOGRAPHY |  | 25 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00912 | DESA SRI PUTERI NO. 2 | OUTGOING 1 | HOTSPOT | CABLE LUG / TERMINATION | OUTGOING 1 - RED PHASE CABLE TERMINATION (25.1 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-26 | 2023-05-26 | 2023-05-26 | FUSE / LINK | REPLACEMENT | MENUKAR GANTI FIUS HOLDER BARU | [7 empty] | 39 | TRUE
180 | 2023-04-17 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00912 | DESA SRI PUTERI NO. 2 | OUTGOING 8 | HOTSPOT | FUSE / LINK | OUTGOING 8 - RED PHASE FUSE LINK (113.5 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-04 | 2023-05-04 | 2023-05-04 | FUSE / LINK | REPLACEMENT | TUKAR DAN GANTI FIUS HOLDER | [7 empty] | 17 | TRUE
181 | 2023-04-17 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00399 | SALAK SOUTH N/VILLAGE NO. 2 | OUTGOING 7 | HOTSPOT | FUSE / LINK | OUTGOING 8 - RED PHASE FUSE LINK (52.8 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-04 | 2023-05-04 | 2023-05-04 | FUSE / LINK | REPLACEMENT | TUKAR DAN GANTI FIUS HOLDER | [7 empty] | 17 | TRUE
182 | 2023-04-17 | AMT SOLUTIONS | THERMOGRAPHY |  | 28 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00405 | SALAK SOUTH N/VILLAGE NO. 1 | OUTGOING 7 | HOTSPOT | FUSE / LINK | OUTGOING 7 - RED PHASE FUSE LINK (28.8 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-04 | 2023-05-04 | 2023-05-04 | FUSE / LINK | REPLACEMENT | TUKAR DAN GANTI FIUS HOLDER | [7 empty] | 17 | TRUE
183 | 2023-04-18 | AMT SOLUTIONS | THERMOGRAPHY |  | 44 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | PILC | WKLS/PCE/J00322 | P/E O.U.G NO.1 | OUTGOING 5 | HOTSPOT | FUSE / LINK | OUTGOING 5 - YELLOW PHASE FUSE LINK (44.8 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-03 | 2023-05-03 | 2023-05-03 | FUSE / LINK | REPLACEMENT | TUKAR DAN GANTI FIUS HOLDER | [7 empty] | 15 | TRUE
184 | 2023-04-18 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | MERLIN GERIN |  | XLPE | WKLS/PCE/J00921 | PDT OUG NO. 1 | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING 6 - RED PHASE FUSE LINK (58.3 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-03 | 2023-05-03 | 2023-05-03 | FUSE / LINK | REPLACEMENT | TUKAR DAN GANTI FIUS HOLDER | [7 empty] | 15 | TRUE
185 | 2023-04-18 | AMT SOLUTIONS | THERMOGRAPHY |  | 30 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00324 | OUG NO. 3 | INCOMING 1 | HOTSPOT | FUSE / LINK | INCOMING 1 - NEUTRAL PHASE LINK (30.0 °C) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-06-07 | 2023-06-07 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 50 | TRUE
186 | 2023-04-18 | AMT SOLUTIONS | THERMOGRAPHY |  | 23 | LVDB / F.PILLAR | RMU SF6 | LUCY | MTM | PILC | WKLS/PCE/J00326 | OUG NO. 6 | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING 6 - RED PHASE FUSE LINK (23.8 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-03 | 2023-05-03 | 2023-05-03 | FUSE / LINK | REPLACEMENT | TUKAR DAN GANTI FIUS HOLDER | [7 empty] | 15 | TRUE
187 | 2023-04-18 | AMT SOLUTIONS | THERMOGRAPHY |  | 22 | LVDB / F.PILLAR | RMU SF6 | LUCY | MTM | XLPE | WKLS/PCE/J00326 | OUG NO. 6 | OUTGOING 8 | HOTSPOT | FUSE / LINK | OUTGOING 8 - RED PHASE FUSE LINK (22.8 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-03 | 2023-05-03 | 2023-05-03 | FUSE / LINK | REPLACEMENT | TUKAR DAN GANTI FIUS HOLDER | [7 empty] | 15 | TRUE
188 | 2023-05-03 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | AICHI | MTM | XLPE | WKLS/PCE/J00749 | TMN SURIA JAYA NO. 1 | OUTGOING 8 | HOTSPOT | FUSE / LINK | OUTGOING 8 - YELLOW PHASE FUSE LINK (63.4 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-19 | 2023-05-19 | 2023-05-19 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
189 | 2023-05-03 | AMT SOLUTIONS | THERMOGRAPHY |  | 35 | LVDB / F.PILLAR | VCB | AICHI | MTM | PILC | WKLS/PCE/J00749 | TMN SURIA JAYA NO. 1 | OUTGOING 8 | HOTSPOT | FUSE / LINK | OUTGOING 8 - YELLOW PHASE FUSE LINK (35.9 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-19 | 2023-05-19 | 2023-05-19 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
190 | 2023-05-03 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TAMCO | EWT | PILC | WKLS/PCE/J00745 | TMN MINANG | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING 8 - RED PHASE FUSE LINK (70.8 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-01 | 2023-06-01 | 2023-06-01 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 29 | TRUE
191 | 2023-05-03 | AMT SOLUTIONS | THERMOGRAPHY |  | 32 | LVDB / F.PILLAR | VCB | TAMCO | EWT | PILC | WKLS/PCE/J00745 | TMN MINANG | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING 8 - YELLOW PHASE FUSE LINK (32.8 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-01 | 2023-06-01 | 2023-06-01 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 29 | TRUE
192 | 2023-05-04 | AMT SOLUTIONS | THERMOGRAPHY |  | 48 | LVDB / F.PILLAR | RMU SF6 | LUCY | MTM | XLPE | WKLS/PCE/J00335 | MASJID JAMEK JLN PUCHONG | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING 6 - BLUE PHASE FUSE LINK (48.0 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-18 | 2023-05-18 | 2023-05-18 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 14 | TRUE
193 | 2023-05-05 | AMT SOLUTIONS | ULTRASOUND | 3 |  | TRANSFORMER | VCB | LKH HSS | MTM | XLPE | WKLS/PCE/J00199 | NO. 1 JLN 10/152 OUG IND PARK | TX1 | TRACKING SOUND | TX CABLE | RED PHASE CABLE TERMINATION (3dB) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-06-08 | 2023-06-08 | TERMINATION | REPLACEMENT | [8 empty] | 34 | TRUE
194 | 2023-05-05 | AMT SOLUTIONS | THERMOGRAPHY |  | 2 | TRANSFORMER | VCB | LKH HSS | MTM | XLPE | WKLS/PCE/J00199 | NO. 1 JLN 10/152 OUG IND PARK | TX1 | HOTSPOT | TX CABLE | RED PHASE CABLE TERMINATION (2.5 °C) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-06-08 | 2023-06-08 | TERMINATION | REPLACEMENT | [8 empty] | 34 | TRUE
195 | 2023-05-05 | AMT SOLUTIONS | THERMOGRAPHY |  | 1 | TRANSFORMER | VCB | LKH HSS | MTM | XLPE | WKLS/PCE/J00199 | NO. 1 JLN 10/152 OUG IND PARK | TX2 | HOTSPOT | TX CABLE | RED, YELLOW & BLUE PHASE CABLE TERMINATION (1.8 °C) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-06-08 | 2023-06-08 | TERMINATION | REPLACEMENT | [8 empty] | 34 | TRUE
196 | 2023-05-06 | AMT SOLUTIONS | ULTRASOUND | 23 |  | SWITCHGEAR | RMU SF6 | F&G INDKOM | MTM | PILC | WKLS/PCE/J00279 | SG KUYOH PUMP HOUSE | 11KV CABLE FEEDER | CORONA DISCHARGE | CABLE COMPARTMENT | CABLE COMP - 6687 P/E KG BOHOL (23dB) | REPAIR IMMEDIATELY | CABLE MAINTENANCE |  | 2023-07-31 | 2023-07-09 | TERMINATION | NONE | Details : Buat sambungan terus kabel antara P/E Kg Bohol dengan P/E Rawat & Rehat Kinrara Arah Timur. Lay kabel baru 150mmp xlpe sebanyak 8m.Buat 2x st joint. Cable masih low reading(kabel ke kg bohol) dan belum batal authorised. Perlu serah pada team PD Mapping/Locate untuk tindakan selanjutnya | [7 empty] | 64 | TRUE
197 | 2023-05-06 | AMT SOLUTIONS | ULTRASOUND | 27 |  | SWITCHGEAR | RMU SF6 | F&G INDKOM | MTM | PILC | WKLS/PCE/J00279 | SG KUYOH PUMP HOUSE | TX PANEL | CORONA DISCHARGE | CABLE COMPARTMENT | FUSE COMP - 6686 TX (27dB) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-12 | 2023-07-12 | RMU | NONE | DISMANTLE PENCAWANG | [7 empty] | 67 | TRUE
198 | 2023-05-06 | AMT SOLUTIONS | THERMOGRAPHY |  | 48 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00277 | BANGUNAN MUTIARA JOHAN PUCHONG | OUTGOING 4 | HOTSPOT | FUSE / LINK | OUTGOING 4 - RED PHASE FUSE LINK (48.7 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-18 | 2023-05-18 | 2023-05-18 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 12 | TRUE
199 | 2023-05-06 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TAMCO | MTM | PILC | WKLS/PCE/J00313 | GUNUNG PETALING | OUTGOING 5 | HOTSPOT | FUSE / LINK | OUTGOING 5 - YELLOW PHASE FUSE LINK (104.8 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-18 | 2023-05-18 | 2023-05-18 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 12 | TRUE
200 | 2023-05-06 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TAMCO | EWT | XLPE | WKLS/PCE/J00314 | PARK MAY (WKLS/PCE/J00315) | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING 6 - YELLOW PHASE FUSE LINK (55.6 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-18 | 2023-05-18 | 2023-05-18 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 12 | TRUE
201 | 2023-05-06 | AMT SOLUTIONS | THERMOGRAPHY |  | 26 | LVDB / F.PILLAR | VCB | AICHI |  | XLPE | WKLS/PCE/J00076 | PUMP HOUSE BT 4 1/2 JLN KLANG LAMA | OUTGOING 1 | HOTSPOT | FUSE / LINK | OUTGOING 1 - YELLOW PHASE FUSE LINK (26.5 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-17 | 2023-05-17 | 2023-05-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 11 | TRUE
202 | 2023-05-06 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | AICHI |  | PILC | WKLS/PCE/J00076 | PUMP HOUSE BT 4 1/2 JLN KLANG LAMA | OUTGOING 2 | HOTSPOT | FUSE / LINK | OUTGOING 2 - RED PHASE FUSE LINK (72.2 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-17 | 2023-05-17 | 2023-05-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 11 | TRUE
203 | 2023-05-06 | AMT SOLUTIONS | THERMOGRAPHY |  | 31 | LVDB / F.PILLAR | VCB | AICHI |  | XLPE | WKLS/PCE/J00076 | PUMP HOUSE BT 4 1/2 JLN KLANG LAMA | OUTGOING 4 | HOTSPOT | FUSE / LINK | OUTGOING 4 - BLUE PHASE FUSE LINK (31.8 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-17 | 2023-05-17 | 2023-05-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 11 | TRUE
204 | 2023-05-06 | AMT SOLUTIONS | THERMOGRAPHY |  | 36 | LVDB / F.PILLAR | VCB | AICHI |  | XLPE | WKLS/PCE/J00076 | PUMP HOUSE BT 4 1/2 JLN KLANG LAMA | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING 6 - RED PHASE FUSE LINK (36.3 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-17 | 2023-05-17 | 2023-05-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 11 | TRUE
205 | 2023-05-07 | AMT SOLUTIONS | THERMOGRAPHY |  | 24 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | PILC | WKLS/PCE/J00283 | TMN YARL NO. 1 | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING 6 - YELLOW PHASE FUSE LINK (24.9 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-17 | 2023-05-17 | 2023-05-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 10 | TRUE
206 | 2023-05-08 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00284 | TMN YARL NO. 2 | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING 6 - RED PHASE FUSE LINK (105.1 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-17 | 2023-05-17 | 2023-05-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
207 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | 10 | LVDB / F.PILLAR | RMU SF6 | SCHNEIDER | EWT | XLPE | WKLS/PCE/J00678 | PADAT KEDAI JLN 13/155B TMN ESPLANAD (X) | OUTGOING 7 | HOTSPOT | FUSE / LINK | OUTGOING 7 - RED PHASE FUSE LINK (10.1 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-01 | 2023-06-01 | 2023-06-01 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 23 | TRUE
208 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | 2 | TRANSFORMER | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00245 | JLN 13/155B TMN ESPLANAD BKT JALIL | TX2 | HOTSPOT | TX CABLE | YELLOW & BLUE PHASE CABLE TERMINATION (2.8 °C) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-06-09 | 2023-06-09 | TERMINATION | REPLACEMENT | [8 empty] | 31 | TRUE
209 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | PILC | WKLS/PCE/J00327 | OUG NO. 2 | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING 6 - YELLOW PHASE FUSE LINK (71.3 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-19 | 2023-05-19 | 2023-05-19 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 10 | TRUE
210 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | 18 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | PILC | WKLS/PCE/J00327 | OUG NO. 2 | OUTGOING 8 | HOTSPOT | FUSE / LINK | OUTGOING 8 - BLUE PHASE FUSE LINK (18.3 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-19 | 2023-05-19 | 2023-05-19 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 10 | TRUE
211 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | 46 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00327 | OUG NO. 2 | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING 6 - RED PHASE FUSE LINK (46.2 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-19 | 2023-05-19 | 2023-05-19 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 10 | TRUE
212 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00327 | OUG NO. 2 | OUTGOING 7 | HOTSPOT | FUSE / LINK | OUTGOING 7 - BLUE PHASE FUSE LINK (71.3 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-19 | 2023-05-19 | 2023-05-19 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 10 | TRUE
213 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TAMCO | MTM | PILC | WKLS/PCE/J00197 | OUG NO. 8 | OUTGOING 5 | HOTSPOT | FUSE / LINK | OUTGOING 5 - YELLOW PHASE FUSE LINK (122.4 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-22 | 2023-05-22 | 2023-05-22 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 13 | TRUE
214 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | 26 | LVDB / F.PILLAR | VCB | TAMCO | MTM | PILC | WKLS/PCE/J00197 | OUG NO. 8 | OUTGOING 7 | HOTSPOT | FUSE / LINK | OUTGOING 7 - RED PHASE FUSE LINK (26.1 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-22 | 2023-05-22 | 2023-05-22 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 13 | TRUE
215 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | XLPE | WKLS/PCE/J00321 | OUG NO. 5 | OUTGOING 1 | HOTSPOT | FUSE / LINK | OUTGOING 1 - BLUE PHASE FUSE LINK (52.2 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-22 | 2023-05-22 | 2023-05-22 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 13 | TRUE
216 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | XLPE | WKLS/PCE/J00321 | OUG NO. 5 | OUTGOING 3 | HOTSPOT | FUSE / LINK | OUTGOING 3 - YELLOW PHASE FUSE LINK (184.2 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-22 | 2023-05-22 | 2023-05-22 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 13 | TRUE
217 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | XLPE | WKLS/PCE/J00321 | OUG NO. 5 | OUTGOING 7 | HOTSPOT | FUSE / LINK | OUTGOING 7 - RED PHASE FUSE LINK (52.1 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-22 | 2023-05-22 | 2023-05-22 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 13 | TRUE
218 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | 24 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | PILC | WKLS/PCE/J00321 | OUG NO. 5 | OUTGOING 4 | HOTSPOT | FUSE / LINK | OUTGOING 4 - NEUTRAL PHASE LINK (24.7 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-22 | 2023-05-22 | 2023-05-22 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 13 | TRUE
219 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | 45 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | XLPE | WKLS/PCE/J00321 | OUG NO. 5 | OUTGOING 7 | HOTSPOT | FUSE / LINK | OUTGOING 7 - YELLOW PHASE FUSE LINK (45.3 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-22 | 2023-05-22 | 2023-05-22 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 13 | TRUE
220 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | 18 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | XLPE | WKLS/PCE/J00321 | OUG NO. 5 | OUTGOING 8 | HOTSPOT | FUSE / LINK | OUTGOING 8 - YELLOW PHASE FUSE LINK (18.2 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-22 | 2023-05-22 | 2023-05-22 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 13 | TRUE
221 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | 18 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | PILC | WKLS/PCE/J00151 | SRI PETALING NO. 4 | OUTGOING 4 | HOTSPOT | FUSE / LINK | OUTGOING 4 - RED PHASE FUSE LINK (18.8 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-22 | 2023-05-22 | 2023-05-22 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 13 | TRUE
222 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | XLPE | WKLS/PCE/J00151 | SRI PETALING NO. 4 | OUTGOING 1 | HOTSPOT | FUSE / LINK | OUTGOING 1 - RED PHASE FUSE LINK (103.3 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-22 | 2023-05-22 | 2023-05-22 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 13 | TRUE
223 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | 36 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | XLPE | WKLS/PCE/J00151 | SRI PETALING NO. 4 | OUTGOING 1 | HOTSPOT | FUSE / LINK | OUTGOING 1 - BLUE PHASE FUSE LINK (36.9 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-22 | 2023-05-22 | 2023-05-22 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 13 | TRUE
224 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | XLPE | WKLS/PCE/J00151 | SRI PETALING NO. 4 | OUTGOING 2 | HOTSPOT | FUSE / LINK | OUTGOING 2 - RED PHASE FUSE LINK (74.2 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-22 | 2023-05-22 | 2023-05-22 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 13 | TRUE
225 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | 44 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | XLPE | WKLS/PCE/J00151 | SRI PETALING NO. 4 | OUTGOING 2 | HOTSPOT | FUSE / LINK | OUTGOING 2 - YELLOW PHASE FUSE LINK (44.6 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-22 | 2023-05-22 | 2023-05-22 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 13 | TRUE
226 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | 35 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | XLPE | WKLS/PCE/J00151 | SRI PETALING NO. 4 | OUTGOING 2 | HOTSPOT | FUSE / LINK | OUTGOING 2 - RED PHASE FUSE LINK (35.2 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-22 | 2023-05-22 | 2023-05-22 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 13 | TRUE
227 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | 44 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | XLPE | WKLS/PCE/J00151 | SRI PETALING NO. 4 | OUTGOING 3 | HOTSPOT | FUSE / LINK | OUTGOING 3 - RED PHASE FUSE LINK (44.8 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-22 | 2023-05-22 | 2023-05-22 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 13 | TRUE
228 | 2023-05-09 | AMT SOLUTIONS | THERMOGRAPHY |  | 30 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | XLPE | WKLS/PCE/J00151 | SRI PETALING NO. 4 | OUTGOING 3 | HOTSPOT | FUSE / LINK | OUTGOING 3 - YELLOW PHASE FUSE LINK (30.5 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-22 | 2023-05-22 | 2023-05-22 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 13 | TRUE
229 | 2023-05-10 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | PILC | WKLS/PCE/J00377 | TMN SRI INDAH NO. 4 | OUTGOING 8 | HOTSPOT | FUSE / LINK | OUTGOING 8 - BLUE PHASE FUSE LINK (60.3 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-05-22 | 2023-05-22 | 2023-05-22 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 12 | TRUE
230 | 2023-05-10 | AMT SOLUTIONS | THERMOGRAPHY |  | 3 | BATTERY | VCB | LKH HSS | MTM |  | WKLS/PCE/J00185 | STADIUM HOKI BKT JALIL | OTHERS | HOTSPOT | OTHERS | BATTERY BODY (3.5 °C) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-06-30 | 2023-06-30 | BATTERY | REPLACEMENT | [8 empty] | 51 | TRUE
231 | 2023-05-11 | AMT SOLUTIONS | ULTRASOUND | 3 |  | TRANSFORMER | VCB | LKH HSS | MTM | PILC | WKLS/PCE/J00189 | STADIUM SQUASH | TX1 | TRACKING SOUND | TX CABLE | RED PHASE CABLE TERMINATION (3dB) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-06-21 | 2023-06-21 | TERMINATION | REPLACEMENT | [8 empty] | 41 | TRUE
232 | 2023-05-13 | AMT SOLUTIONS | THERMOGRAPHY |  | 17 | INCOMING LINK | VCB | TOSHIBA | LKH | XLPE | WKLS/PCE/J00381 | SRI PETALING JLN 3/149 J ZON L2 | INCOMING 1 | HOTSPOT | FUSE / LINK | INCOMING 1 - RED PHASE LINK (17.7 °C) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-06-13 | 2023-06-13 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 31 | TRUE
233 | 2023-05-13 | AMT SOLUTIONS | THERMOGRAPHY |  | 20 | INCOMING LINK | VCB | TOSHIBA | LKH | XLPE | WKLS/PCE/J00381 | SRI PETALING JLN 3/149 J ZON L2 | INCOMING 2 | HOTSPOT | FUSE / LINK | INCOMING 2 - RED PHASE LINK (20.8 °C) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-06-13 | 2023-06-13 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 31 | TRUE
234 | 2023-05-13 | AMT SOLUTIONS | THERMOGRAPHY |  | 30 | INCOMING LINK | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01313 | KEDAI PEJABAT 2TKT JLN TUN PERAK | INCOMING 1 | HOTSPOT | FUSE / LINK | INCOMING 1 - YELLOW PHASE LINK (30.9 °C) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-06-13 | 2023-06-13 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 31 | TRUE
235 | 2023-05-13 | AMT SOLUTIONS | ULTRASOUND | 23 |  | SWITCHGEAR | VCB | UNIVAC | MTM | XLPE | WKLS/PCE/J00957 | P/PURI WIRA TMN TUN PERAK | TX PANEL | TRACKING SOUND | CABLE COMPARTMENT | CABLE COMP - 31092 TX1 (23dB) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-06-12 | 2023-06-12 | VCB | REPLACEMENT | TUKAR S/GEAR VCB UNIVAC KE S/GEAR VCB TOSHIBA SERTA CABLE HT TX | [7 empty] | 30 | TRUE
236 | 2023-05-14 | AMT SOLUTIONS | THERMOGRAPHY |  | 2 | TRANSFORMER | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00666 | KEDAI/PEJ FASA 2C ALAM DAMAI | TX1 | HOTSPOT | TX CABLE | BLUE PHASE CABLE TERMINATION (2.6 °C) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-06-10 | 2023-06-10 | TERMINATION | REPLACEMENT | [8 empty] | 27 | TRUE
237 | 2023-05-15 | AMT SOLUTIONS | THERMOGRAPHY |  | 24 | BATTERY | VCB | SIEMENS | MTM |  | WKLS/PCE/J00175 | MEGAN PHEONIX | OTHERS | HOTSPOT | OTHERS | BATTERY BODY (24.7 °C) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-10-12 | 2023-10-12 | BATTERY | REPLACEMENT | [8 empty] | 150 | TRUE
238 | 2023-05-15 | AMT SOLUTIONS | THERMOGRAPHY |  | 13 | INCOMING LINK | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00755 | TMN CONNAUGHT NO. 3 | INCOMING 1 | HOTSPOT | FUSE / LINK | INCOMING 1 - RED PHASE LINK (13.8 °C) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-06-07 | 2023-06-07 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 23 | TRUE
239 | 2023-05-15 | AMT SOLUTIONS | THERMOGRAPHY |  | 15 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00755 | TMN CONNAUGHT NO. 3 | OUTGOING 1 | HOTSPOT | FUSE / LINK | OUTGOING 1 - YELLOW PHASE FUSE LINK (15.8 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-01 | 2023-06-01 | 2023-06-01 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 17 | TRUE
240 | 2023-05-15 | AMT SOLUTIONS | THERMOGRAPHY |  | 27 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | PILC | WKLS/PCE/J00755 | TMN CONNAUGHT NO. 3 | OUTGOING 2 | HOTSPOT | FUSE / LINK | OUTGOING 2 - BLUE PHASE FUSE LINK (27.6 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-01 | 2023-06-01 | 2023-06-01 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 17 | TRUE
241 | 2023-05-15 | AMT SOLUTIONS | THERMOGRAPHY |  | 29 | BATTERY | RMU MOTORIZED | LUCY | MTM |  | WKLS/PCE/J00254 | DESA TUN RAZAK C | OTHERS | HOTSPOT | OTHERS | BATTERY BODY (29.9 °C) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-10-12 | 2023-10-12 | BATTERY | TIGHTNESS INSPECTION | [8 empty] | 150 | TRUE
242 | 2023-05-16 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | ITEM | MTM | XLPE | WKLS/PCE/J00149 | DESA TUN RAZAK APT | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING 6 - RED PHASE FUSE LINK (62.2 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-01 | 2023-06-01 | 2023-06-01 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
243 | 2023-05-16 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | ITEM | MTM | XLPE | WKLS/PCE/J00149 | DESA TUN RAZAK APT | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING 6 - YELLOW PHASE FUSE LINK (110.9 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-01 | 2023-06-01 | 2023-06-01 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
244 | 2023-05-16 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | PILC | WKLS/PCE/J00407 | TAMAN SG.BESI NO.3 | OUTGOING 1 | HOTSPOT | FUSE / LINK | OUTGOING 1 - RED PHASE FUSE LINK (54.3 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-03 | 2023-06-03 | 2023-06-03 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 18 | TRUE
245 | 2023-05-16 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | PILC | WKLS/PCE/J00407 | TAMAN SG.BESI NO.3 | OUTGOING 3 | HOTSPOT | FUSE / LINK | OUTGOING 3 - YELLOW PHASE FUSE LINK (62.1 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-03 | 2023-06-03 | 2023-06-03 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 18 | TRUE
246 | 2023-05-16 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | PILC | WKLS/PCE/J00407 | TAMAN SG.BESI NO.3 | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING 6 - YELLOW PHASE FUSE LINK (63.1 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-03 | 2023-06-03 | 2023-06-03 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 18 | TRUE
247 | 2023-05-16 | AMT SOLUTIONS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00407 | TAMAN SG.BESI NO.3 | OUTGOING 1 | HOTSPOT | FUSE / LINK | OUTGOING 1 - BLUE PHASE FUSE LINK (63.4 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-03 | 2023-06-03 | 2023-06-03 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 18 | TRUE
248 | 2023-05-16 | AMT SOLUTIONS | THERMOGRAPHY |  | 36 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00168 | NO.2 PAKAR IND. PARK SUNGAI BESI | OUTGOING 7 | HOTSPOT | FUSE / LINK | OUTGOING 7 - RED PHASE FUSE LINK (36.9 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-03 | 2023-06-03 | 2023-06-03 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 18 | TRUE
249 | 2023-05-16 | AMT SOLUTIONS | THERMOGRAPHY |  | 38 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00493 | JKR QUARTERS SALAK SOUTH | OUTGOING 5 | HOTSPOT | FUSE / LINK | OUTGOING 5 - YELLOW PHASE FUSE LINK (38.8 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-03 | 2023-06-03 | 2023-06-03 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 18 | TRUE
250 | 2023-05-17 | AMT SOLUTIONS | THERMOGRAPHY |  | 34 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00041 | CHERAS BARU NO. 5 | OUTGOING 5 | HOTSPOT | FUSE / LINK | OUTGOING 5 - BLUE PHASE FUSE LINK (34.8 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-03 | 2023-06-03 | 2023-06-03 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 17 | TRUE
251 | 2023-05-17 | AMT SOLUTIONS | THERMOGRAPHY |  | 38 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00041 | CHERAS BARU NO. 5 | OUTGOING 8 | HOTSPOT | FUSE / LINK | OUTGOING 8 - BLUE PHASE FUSE LINK (38.9 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-03 | 2023-06-03 | 2023-06-03 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 17 | TRUE
252 | 2023-05-17 | AMT SOLUTIONS | THERMOGRAPHY |  | 38 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00041 | CHERAS BARU NO. 5 | OUTGOING 2 | HOTSPOT | FUSE / LINK | OUTGOING 2 - RED PHASE FUSE LINK (38.4 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-03 | 2023-06-03 | 2023-06-03 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 17 | TRUE
253 | 2023-05-17 | AMT SOLUTIONS | THERMOGRAPHY |  | 17 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00041 | CHERAS BARU NO. 5 | OUTGOING 2 | HOTSPOT | FUSE / LINK | OUTGOING 2 - BLUE PHASE FUSE LINK (17.4 °C) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-03 | 2023-06-03 | 2023-06-03 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 17 | TRUE
254 | 2023-05-23 | INFRAKOMAS | THERMOGRAPHY |  | 1 | SWITCHGEAR | RMU SF6 | FALCON BETA | SGB | XLPE | WKLS/PCE/J01119 | BLK B CASA DESA KONDO | 11KV CABLE FEEDER | HOTSPOT | CABLE COMPARTMENT | HOTSPOT DETECTED AT RMU SF6: FEEDER 38845 TX 1 - BUSHING | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-08 | 2023-07-08 | TERMINATION | REPLACEMENT | [8 empty] | 46 | TRUE
255 | 2023-05-23 | INFRAKOMAS | THERMOGRAPHY |  | 12 | TRANSFORMER | RMU SF6 | FALCON BETA | SGB | XLPE | WKLS/PCE/J01119 | BLK B CASA DESA KONDO | TX1 | HOTSPOT | TX CABLE | HOTSPOT AT TX 1: HV SIDE - RED PHASE CABLE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-08 | 2023-07-08 | TERMINATION | REPLACEMENT | [8 empty] | 46 | TRUE
256 | 2023-06-01 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | LKH HSS | MTM | XLPE | WKLS/PCE/J00016 | BKT OUG TOWN HOUSE NO. 1 | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F2 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-17 | 2023-06-17 | 2023-06-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
257 | 2023-06-01 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | VCB | LKH HSS | MTM | XLPE | WKLS/PCE/J00016 | BKT OUG TOWN HOUSE NO. 1 | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F2 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-17 | 2023-06-17 | 2023-06-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
258 | 2023-06-01 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | LKH HSS | MTM | XLPE | WKLS/PCE/J00016 | BKT OUG TOWN HOUSE NO. 1 | OUTGOING 1 | HOTSPOT | CABLE LUG / TERMINATION | HOTSPOT AT LVDB (TX 2): OUTGOING F1 - BLUE PHASE CABLE LUG | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-17 | 2023-06-17 | 2023-06-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
259 | 2023-06-01 | INFRAKOMAS | THERMOGRAPHY |  | 47 | LVDB / F.PILLAR | VCB | LKH HSS | MTM | XLPE | WKLS/PCE/J00016 | BKT OUG TOWN HOUSE NO. 1 | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F2 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-17 | 2023-06-17 | 2023-06-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
260 | 2023-06-01 | INFRAKOMAS | THERMOGRAPHY |  | 24 | LVDB / F.PILLAR | VCB | LKH HSS | MTM | XLPE | WKLS/PCE/J00016 | BKT OUG TOWN HOUSE NO. 1 | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F4 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-17 | 2023-06-17 | 2023-06-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
261 | 2023-06-01 | INFRAKOMAS | THERMOGRAPHY |  | 45 | LVDB / F.PILLAR | VCB | EPE | MTM | XLPE | WKLS/PCE/J00015 | BKT OUG TOWN HOUSE NO. 2 | OUTGOING 1 | HOTSPOT | CABLE LUG / TERMINATION | HOTSPOT AT LVDB (TX 2): OUTGOING F1 - BLUE PHASE CABLE LUG | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-17 | 2023-06-17 | 2023-06-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
262 | 2023-06-01 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | EPE | MTM | XLPE | WKLS/PCE/J00015 | BKT OUG TOWN HOUSE NO. 2 | OUTGOING 2 | HOTSPOT | CABLE LUG / TERMINATION | HOTSPOT AT LVDB (TX 2): OUTGOING F2 - YELLOW PHASE CABLE LUG | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-17 | 2023-06-17 | 2023-06-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
263 | 2023-06-01 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00014 | BKT OUG TOWN HOUSE NO. 3 | OUTGOING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F1 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-17 | 2023-06-17 | 2023-06-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
264 | 2023-06-01 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00014 | BKT OUG TOWN HOUSE NO. 3 | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F2 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-17 | 2023-06-17 | 2023-06-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
265 | 2023-06-01 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00014 | BKT OUG TOWN HOUSE NO. 3 | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F2 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-17 | 2023-06-17 | 2023-06-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
266 | 2023-06-01 | INFRAKOMAS | THERMOGRAPHY |  | 48 | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00014 | BKT OUG TOWN HOUSE NO. 3 | OUTGOING 2 | HOTSPOT | OTHERS | HOTSPOT AT LVDB (TX 1): OUTGOING F2 - YELLOW PHASE CABLE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-17 | 2023-06-17 | 2023-06-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
267 | 2023-06-01 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00014 | BKT OUG TOWN HOUSE NO. 3 | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F2 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-17 | 2023-06-17 | 2023-06-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
268 | 2023-06-01 | INFRAKOMAS | THERMOGRAPHY |  | 45 | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00014 | BKT OUG TOWN HOUSE NO. 3 | OUTGOING 1 | HOTSPOT | CABLE LUG / TERMINATION | HOTSPOT AT LVDB (TX 2): OUTGOING F1 - RED PHASE CABLE LUG | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-17 | 2023-06-17 | 2023-06-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
269 | 2023-06-01 | INFRAKOMAS | THERMOGRAPHY |  | 25 | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00014 | BKT OUG TOWN HOUSE NO. 3 | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F2 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-17 | 2023-06-17 | 2023-06-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
270 | 2023-06-02 | INFRAKOMAS | THERMOGRAPHY |  | 24 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | XLPE | WKLS/PCE/J00289 | TMN IND BKT OUG NO. 3 | OUTGOING 2 | HOTSPOT | FUSE / LINK | HTOSPOT AT LVFP (TX 1): OUTGOING F2 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-17 | 2023-06-17 | 2023-06-17 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 15 | TRUE
271 | 2023-06-02 | INFRAKOMAS | THERMOGRAPHY |  | 2 | TRANSFORMER | VCB | ALTENA | EWT | XLPE | WKLS/PCE/J00564 | BLK E P/PURI KOS RENDAH KG MUHIBBAH | TX1 | HOTSPOT | TX CABLE | HOTSPOT AT TX: HV SIDE - BLUE PHASE CABLE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-20 | 2023-07-20 | CABLE END TO END | REPLACEMENT | Action Taken - Tukar suisgear VCB Altena 2+1 ke suisgear VCB Tamco Scada-Ready 2+1 - Preventive Maintenance TX Hermatically Sealed 1000KVA - 2x term cable XLPE 240MMP - 6x term cable XLPE 70MMP - Wiring Scada pada suisgear VCB - Wiring efi EMG 2nos - Tukar 1 Battery Charger baru - Stensil nama pencawang pada suisgear VCB - Tutup lubang kabel menggunakan fibre plate dan sealent - Check amps, voltage & phase rotation - Normalise | [7 empty] | 48 | TRUE
272 | 2023-06-03 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | TOSHIBA | MTM | XLPE | WKLS/PCE/J00336 | RMH KEDAI TMN SENTOSA | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB: OUTGOING F2 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-10 | 2023-06-10 | 2023-06-10 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 7 | TRUE
273 | 2023-06-03 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | TOSHIBA | MTM | XLPE | WKLS/PCE/J00336 | RMH KEDAI TMN SENTOSA | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB: OUTGOING F4 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-10 | 2023-06-10 | 2023-06-10 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 7 | TRUE
274 | 2023-06-03 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | TOSHIBA | MTM | XLPE | WKLS/PCE/J00336 | RMH KEDAI TMN SENTOSA | OUTGOING 4 | HOTSPOT | CABLE LUG / TERMINATION | HOTSPOT AT LVDB: OUTGOING F4 - YELLOW PHASE CABLE LUG | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-10 | 2023-06-10 | 2023-06-10 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 7 | TRUE
275 | 2023-06-03 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | TOSHIBA | MTM | XLPE | WKLS/PCE/J00336 | RMH KEDAI TMN SENTOSA | OUTGOING 4 | HOTSPOT | CABLE LUG / TERMINATION | HOTSPOT AT LVDB: OUTGOING F4 - BLUE PHASE CABLE LUG | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-10 | 2023-06-10 | 2023-06-10 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 7 | TRUE
276 | 2023-06-03 | INFRAKOMAS | ULTRASOUND | 1 |  | SWITCHGEAR | RMU SF6 | TAMCO | MITSUBISHI | XLPE | WKLS/PCE/J00333 | KG SERI SENTOSA | 11KV CABLE FEEDER | CORONA DISCHARGE | CABLE COMPARTMENT | CORONA SOUND AT RMU SF6: FEEDER 49933 LOOPING - CABLE COMPARTMENT | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-31 | 2023-07-31 | RMU | NONE | defect berulang | [7 empty] | 58 | TRUE
277 | 2023-06-04 | INFRAKOMAS | THERMOGRAPHY |  | 35 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | PILC | WKLS/PCE/J00296 | TMN PANTAI INDAH | OUTGOING 3 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F3 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-20 | 2023-06-20 | 2023-06-20 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
278 | 2023-06-07 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | TOPRANK | MTM | XLPE | WKLS/PCE/J00589 | KEDAI/PEJ JLN PERMAISURI 6 | OUTGOING 3 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1 - 6A): OUTGOING F3 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-19 | 2023-06-19 | 2023-06-19 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 12 | TRUE
279 | 2023-06-07 | INFRAKOMAS | THERMOGRAPHY |  | 20 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J00497 | BT. KONG NO.2 | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F4 - BLUE PHASE FUSE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-19 | 2023-06-19 | 2023-06-19 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 12 | TRUE
280 | 2023-06-07 | INFRAKOMAS | THERMOGRAPHY |  | 36 | BATTERY | VCB | EPE | MTM |  | WKLS/PCE/J00066 | BLK C CEMARA APT BDR SRI PERMAISURI | OTHERS | HOTSPOT | OTHERS | HOTSPOT AT BATTERY CHARGER 2 - TERMINAL CONNECTION | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-10-12 | 2023-10-12 | BATTERY | TIGHTNESS INSPECTION | [8 empty] | 127 | TRUE
281 | 2023-06-07 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00945 | SEK REN MEN KEB SRI TASIK BDR SRI PERMAI | OUTGOING 7 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB: OUTGOING F7 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-19 | 2023-06-19 | 2023-06-19 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 12 | TRUE
282 | 2023-06-07 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | EWT | XLPE | WKLS/PCE/J00495 | SALAK SOUTH TOWN | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP (TX 1): OUTGOING F4 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-20 | 2023-06-20 | 2023-06-20 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 13 | TRUE
283 | 2023-06-08 | INFRAKOMAS | ULTRASOUND | 1 |  | SWITCHGEAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01238 | KUARTERS HOSPITAL REHABILITASI CHERAS | TX PANEL | CORONA DISCHARGE | CABLE COMPARTMENT | CORONA SOUND AT RMU SF6: FEEDER 43595 TX NO.1 - FUSE COMPARTMENT | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-21 | 2023-07-21 | FUSE / LINK | TIGHTNESS INSPECTION | Action Taken | [7 empty] | 43 | TRUE
284 | 2023-06-09 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | PILC | WKLS/PCE/J00822 | BDR TAR FLAT NO. 1 | OUTGOING 6 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB: OUTGOING F6 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-21 | 2023-06-21 | 2023-06-21 | FUSE / LINK | REPLACEMENT | #NAME? | [7 empty] | 12 | TRUE
285 | 2023-06-09 | INFRAKOMAS | THERMOGRAPHY |  | 44 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | EWT | PILC | WKLS/PCE/J00687 | TMN MIDAH NO. 3 | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB: OUTGOING F5 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-21 | 2023-06-21 | 2023-06-21 | FUSE / LINK | REPLACEMENT | #NAME? | [7 empty] | 12 | TRUE
286 | 2023-06-09 | INFRAKOMAS | THERMOGRAPHY |  | 22 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | PILC | WKLS/PCE/J00824 | BDR TAR NO. 2 | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F4 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-21 | 2023-06-21 | 2023-06-21 | FUSE / LINK | REPLACEMENT | #NAME? | [7 empty] | 12 | TRUE
287 | 2023-06-10 | INFRAKOMAS | THERMOGRAPHY |  | 1 | SWITCHGEAR | RMU SF6 | SCHNEIDER | MTM | XLPE | WKLS/PCE/J00827 | BDR TAR FLAT NO. 2 | 11KV CABLE FEEDER | HOTSPOT | CABLE COMPARTMENT | HOTSPOT AT RMU SF6: FEEDER 7482 PE FLAT DBKL JLN BUDIMAN 1 - CABLE COMPARTMENT | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-06 | 2023-09-06 | RMU | REPLACEMENT | DEFECT BERULANG. CADANGAN TUKAR GEAR | [7 empty] | 88 | TRUE
288 | 2023-06-10 | INFRAKOMAS | THERMOGRAPHY |  | 28 | LVDB / F.PILLAR | RMU SF6 | SCHNEIDER | MTM | PILC | WKLS/PCE/J00827 | BDR TAR FLAT NO. 2 | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP (TX 1): OUTGOING F2 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-21 | 2023-06-21 | 2023-06-21 | FUSE / LINK | REPLACEMENT | #NAME? | [7 empty] | 11 | TRUE
289 | 2023-06-10 | INFRAKOMAS | THERMOGRAPHY |  | 50 | LVDB / F.PILLAR | RMU SF6 | SCHNEIDER | MTM | XLPE | WKLS/PCE/J00827 | BDR TAR FLAT NO. 2 | OUTGOING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F1 - BLUE PHASE CABLE CONNECTION (BOLT & NUT) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-21 | 2023-06-21 | 2023-06-21 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 11 | TRUE
290 | 2023-06-10 | INFRAKOMAS | THERMOGRAPHY |  | 20 | LVDB / F.PILLAR | RMU SF6 | SCHNEIDER | MTM | PILC | WKLS/PCE/J00827 | BDR TAR FLAT NO. 2 | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F4 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-21 | 2023-06-21 | 2023-06-21 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 11 | TRUE
291 | 2023-06-10 | INFRAKOMAS | THERMOGRAPHY |  | 19 | LVDB / F.PILLAR | RMU SF6 | SCHNEIDER | MTM | PILC | WKLS/PCE/J00827 | BDR TAR FLAT NO. 2 | OUTGOING 4 | HOTSPOT | CABLE LUG / TERMINATION | HOTSPOT AT LVDB (TX 2): OUTGOING F4 - YELLOW PHASE CABLE CONNECTION (BOLT & NUT) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-21 | 2023-06-21 | 2023-06-21 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 11 | TRUE
292 | 2023-06-10 | INFRAKOMAS | THERMOGRAPHY |  | 28 | LVDB / F.PILLAR | RMU SF6 | SCHNEIDER | MTM | PILC | WKLS/PCE/J00827 | BDR TAR FLAT NO. 2 | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F5 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-21 | 2023-06-21 | 2023-06-21 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 11 | TRUE
293 | 2023-06-10 | INFRAKOMAS | THERMOGRAPHY |  | 9 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | EWT | PILC | WKLS/PCE/J00828 | TMN MULIA NO. 1 | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F4 - YELLOW PHASE CABLE CONNECTION (BOLT & NUT) | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-21 | 2023-06-21 | 2023-06-21 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 11 | TRUE
294 | 2023-06-10 | INFRAKOMAS | THERMOGRAPHY |  | 44 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | EWT | PILC | WKLS/PCE/J00828 | TMN MULIA NO. 1 | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F5 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-21 | 2023-06-21 | 2023-06-21 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 11 | TRUE
295 | 2023-06-10 | INFRAKOMAS | THERMOGRAPHY |  | 12 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | EWT | PILC | WKLS/PCE/J00828 | TMN MULIA NO. 1 | OUTGOING 7 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP (TX 2): OUTGOING F7 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-21 | 2023-06-21 | 2023-06-21 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 11 | TRUE
296 | 2023-06-13 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01210 | MEDAN NIAGA TASIK DAMAI 2 | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F5 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-29 | 2023-06-29 | 2023-06-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
297 | 2023-06-13 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01210 | MEDAN NIAGA TASIK DAMAI 2 | OUTGOING 6 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F6 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-29 | 2023-06-29 | 2023-06-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
298 | 2023-06-13 | INFRAKOMAS | THERMOGRAPHY |  | 12 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01210 | MEDAN NIAGA TASIK DAMAI 2 | OUTGOING 6 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F6 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-29 | 2023-06-29 | 2023-06-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
299 | 2023-06-13 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01210 | MEDAN NIAGA TASIK DAMAI 2 | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F8 - RED PHASE FUSE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-29 | 2023-06-29 | 2023-06-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
300 | 2023-06-13 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01210 | MEDAN NIAGA TASIK DAMAI 2 | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F8 - YELLOW PHASE FUSE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-29 | 2023-06-29 | 2023-06-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
301 | 2023-06-13 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01210 | MEDAN NIAGA TASIK DAMAI 2 | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F8 - BLUE PHASE FUSE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-29 | 2023-06-29 | 2023-06-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
302 | 2023-06-13 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01211 | MEDAN NIAGA TASIK DAMAI 3 | OUTGOING 3 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F3 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-29 | 2023-06-29 | 2023-06-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
303 | 2023-06-13 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01211 | MEDAN NIAGA TASIK DAMAI 3 | OUTGOING 3 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F3 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-29 | 2023-06-29 | 2023-06-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
304 | 2023-06-13 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01211 | MEDAN NIAGA TASIK DAMAI 3 | OUTGOING 3 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F3 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-29 | 2023-06-29 | 2023-06-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
305 | 2023-06-13 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01211 | MEDAN NIAGA TASIK DAMAI 3 | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F4 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-29 | 2023-06-29 | 2023-06-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
306 | 2023-06-13 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01211 | MEDAN NIAGA TASIK DAMAI 3 | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F4 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-29 | 2023-06-29 | 2023-06-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
307 | 2023-06-13 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01211 | MEDAN NIAGA TASIK DAMAI 3 | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F4 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-29 | 2023-06-29 | 2023-06-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
308 | 2023-06-14 | INFRAKOMAS | THERMOGRAPHY |  | 4 | TRANSFORMER | VCB | EPE | MTM | XLPE | WKLS/PCE/J00740 | TMN ANGGERIK NO. 2 | TX1 | HOTSPOT | FUSE / LINK | HOTSPOT AT TX 1: LV SIDE - YELLOW PHASE BUSHING | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-27 | 2023-07-27 | TX LV BUSHING | REPLACEMENT | [8 empty] | 43 | TRUE
309 | 2023-06-14 | INFRAKOMAS | THERMOGRAPHY |  | 21 | LVDB / F.PILLAR | VCB | EPE | MTM | XLPE | WKLS/PCE/J00740 | TMN ANGGERIK NO. 2 | OUTGOING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F1 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-29 | 2023-06-29 | 2023-06-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 15 | TRUE
310 | 2023-06-14 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | EPE | MTM | XLPE | WKLS/PCE/J00740 | TMN ANGGERIK NO. 2 | OUTGOING 3 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F3 - BLUE PHASE CABLE LUG | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-29 | 2023-06-29 | 2023-06-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 15 | TRUE
311 | 2023-06-14 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | VCB | EPE | MTM | XLPE | WKLS/PCE/J00740 | TMN ANGGERIK NO. 2 | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F8 - RED PHASE FUSE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-29 | 2023-06-29 | 2023-06-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 15 | TRUE
312 | 2023-06-14 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | VCB | EPE | MTM | XLPE | WKLS/PCE/J00740 | TMN ANGGERIK NO. 2 | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F8 - YELLOW PHASE FUSE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-29 | 2023-06-29 | 2023-06-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 15 | TRUE
313 | 2023-06-14 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | VCB | EPE | MTM | XLPE | WKLS/PCE/J00740 | TMN ANGGERIK NO. 2 | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F8 - BLUE PHASE FUSE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-29 | 2023-06-29 | 2023-06-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 15 | TRUE
314 | 2023-06-14 | INFRAKOMAS | THERMOGRAPHY |  | 7 | TRANSFORMER | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00240 | TMN BKT ANGSANA NO. 2 | TX1 | HOTSPOT | FUSE / LINK | HOTSPOT AT TX 1: LV SIDE - RED PHASE CABLE LUG | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-13 | 2023-07-13 | TX LV BUSHING | TIGHTNESS INSPECTION | [8 empty] | 29 | TRUE
315 | 2023-06-14 | INFRAKOMAS | THERMOGRAPHY |  | 3 | TRANSFORMER | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00240 | TMN BKT ANGSANA NO. 2 | TX1 | HOTSPOT | FUSE / LINK | HOTSPOT AT TX 1: LV SIDE - BLUE PHASE CABLE LUG | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-13 | 2023-07-13 | TX LV BUSHING | TIGHTNESS INSPECTION | [8 empty] | 29 | TRUE
316 | 2023-06-14 | INFRAKOMAS | THERMOGRAPHY |  | 20 | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00240 | TMN BKT ANGSANA NO. 2 | INCOMING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP (TX 2): INCOMING 2 - YELLOW PHASE LINK | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-13 | 2023-07-13 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 29 | TRUE
317 | 2023-06-14 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00240 | TMN BKT ANGSANA NO. 2 | INCOMING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP (TX 2): INCOMING 2 - BLUE PHASE LINK | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-13 | 2023-07-13 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 29 | TRUE
318 | 2023-06-14 | INFRAKOMAS | THERMOGRAPHY |  | 28 | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00240 | TMN BKT ANGSANA NO. 2 | OUTGOING 3 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP (TX 2): OUTGOING F3 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-29 | 2023-06-29 | 2023-06-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 15 | TRUE
319 | 2023-06-14 | INFRAKOMAS | THERMOGRAPHY |  | 23 | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00240 | TMN BKT ANGSANA NO. 2 | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP (TX 2): OUTGOING F8 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-29 | 2023-06-29 | 2023-06-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 15 | TRUE
320 | 2023-06-26 | INFRAKOMAS | THERMOGRAPHY |  | 37 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | PILC | WKLS/PCE/J00406 | TMN. SG. BESI NO 2 | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F2 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-07 | 2023-07-07 | 2023-07-07 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 11 | TRUE
321 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | 5 | TRANSFORMER | RMU SF6 | F&G INDKOM | SGB | XLPE | WKLS/PCE/J00521 | THONG HIN STEEL MILL | TX1 | HOTSPOT | CABLE LUG / TERMINATION | HOTSPOT AT TX: LV SIDE - RED PHASE CABLE LUG | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-23 | 2023-07-23 | TX LV BUSHING | TIGHTNESS INSPECTION | [8 empty] | 26 | TRUE
322 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | SGB | XLPE | WKLS/PCE/J00521 | THONG HIN STEEL MILL | INCOMING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: INCOMING 1 - BLUE PHASE LINK | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-23 | 2023-07-23 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 26 | TRUE
323 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | 46 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | SGB | XLPE | WKLS/PCE/J00521 | THONG HIN STEEL MILL | INCOMING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: INCOMING 2 - BLUE PHASE LINK | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-23 | 2023-07-23 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 26 | TRUE
324 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | SGB | XLPE | WKLS/PCE/J00521 | THONG HIN STEEL MILL | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F2 - BLUE PHASE FUSE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-06 | 2023-07-06 | 2023-07-06 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
325 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | SGB | XLPE | WKLS/PCE/J00521 | THONG HIN STEEL MILL | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F8 - RED PHASE FUSE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-06 | 2023-07-06 | 2023-07-06 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
326 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | SGB | XLPE | WKLS/PCE/J00521 | THONG HIN STEEL MILL | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F8 - YELLOW PHASE FUSE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-06 | 2023-07-06 | 2023-07-06 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
327 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | SGB | XLPE | WKLS/PCE/J00521 | THONG HIN STEEL MILL | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F8 - BLUE PHASE FUSE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-06 | 2023-07-06 | 2023-07-06 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
328 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | 37 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00525 | GOVERMENT PRINTING NO. 1 | INCOMING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): INCOMING 1 - NEUTRAL LINK (BOLT & NUT) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-23 | 2023-07-23 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 26 | TRUE
329 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | 31 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00525 | GOVERMENT PRINTING NO. 1 | INCOMING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): INCOMING 2 - BLUE PHASE LINK (BOLT & NUT) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-23 | 2023-07-23 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 26 | TRUE
330 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | 31 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00525 | GOVERMENT PRINTING NO. 1 | OUTGOING 3 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F3 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-06 | 2023-07-06 | 2023-07-06 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
331 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU OIL | TAMCO | MTM | XLPE | WKLS/PCE/J00515 | SUM POH ENGINEERING | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB: OUTGOING F4 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-06 | 2023-07-06 | 2023-07-06 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
332 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | 20 | LVDB / F.PILLAR | RMU OIL | TAMCO | MTM | XLPE | WKLS/PCE/J00515 | SUM POH ENGINEERING | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB: OUTGOING F4 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-06 | 2023-07-06 | 2023-07-06 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
333 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01010 | CHERAS BARU NO. 1 | INCOMING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: INCOMING - NEUTRAL LINK | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-16 | 2023-07-16 | FUSE / LINK | TIGHTNESS INSPECTION | Action Taken - Gosok dan ketatkan skru link incoming NEUTRAL - Check amps, voltage & phase rotation - Normalise | [7 empty] | 19 | TRUE
334 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01010 | CHERAS BARU NO. 1 | OUTGOING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F1 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-05 | 2023-07-05 | 2023-07-05 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 8 | TRUE
335 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | 22 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01010 | CHERAS BARU NO. 1 | OUTGOING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F1 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-05 | 2023-07-05 | 2023-07-05 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 8 | TRUE
336 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01010 | CHERAS BARU NO. 1 | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F4 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-05 | 2023-07-05 | 2023-07-05 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 8 | TRUE
337 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | 3 | TRANSFORMER | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01011 | CHERAS BARU NO. 2 | TX1 | HOTSPOT | TX BUSHING | HOTSPOT AT TX: LV SIDE - RED PHASE BUSHING | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-16 | 2023-07-16 | TX LV BUSHING | TIGHTNESS INSPECTION | Action Taken - Gosok dan ketatkan skru cable lug cable lv TX - Gosok dan ketatkan skru link incoming red, yellow & blue phase. - Ketatka skru TOP DEMAND CABLE CONNECTION - Check amps, voltage & phase rotation - Normalise | [7 empty] | 19 | TRUE
338 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | 4 | TRANSFORMER | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01011 | CHERAS BARU NO. 2 | TX1 | HOTSPOT | TX BUSHING | HOTSPOT AT TX: LV SIDE - YELLOW PHASE BUSHING | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-16 | 2023-07-16 | TX LV BUSHING | TIGHTNESS INSPECTION | Action Taken - Gosok dan ketatkan skru cable lug cable lv TX - Gosok dan ketatkan skru link incoming red, yellow & blue phase. - Ketatka skru TOP DEMAND CABLE CONNECTION - Check amps, voltage & phase rotation - Normalise | [7 empty] | 19 | TRUE
339 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01011 | CHERAS BARU NO. 2 | OTHERS | HOTSPOT | LV WIRING CONTACT | HOTSPOT AT LVFP: TOP DEMAND CABLE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-05 | 2023-07-05 | 2023-07-05 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 8 | TRUE
340 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01011 | CHERAS BARU NO. 2 | INCOMING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: INCOMING 2 - RED PHASE LINK | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-16 | 2023-07-16 | FUSE / LINK | CLEANING | Action Taken - Gosok dan ketatkan skru cable lug cable lv TX - Gosok dan ketatkan skru link incoming red, yellow & blue phase. - Ketatka skru TOP DEMAND CABLE CONNECTION - Check amps, voltage & phase rotation - Normalise | [7 empty] | 19 | TRUE
341 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01011 | CHERAS BARU NO. 2 | INCOMING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: INCOMING 2 - YELLOW PHASE LINK | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-16 | 2023-07-16 | FUSE / LINK | CLEANING | Action Taken - Gosok dan ketatkan skru cable lug cable lv TX - Gosok dan ketatkan skru link incoming red, yellow & blue phase. - Ketatka skru TOP DEMAND CABLE CONNECTION - Check amps, voltage & phase rotation - Normalise | [7 empty] | 19 | TRUE
342 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01011 | CHERAS BARU NO. 2 | INCOMING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: INCOMING 2 - BLUE PHASE LINK | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-16 | 2023-07-16 | FUSE / LINK | CLEANING | Action Taken - Gosok dan ketatkan skru cable lug cable lv TX - Gosok dan ketatkan skru link incoming red, yellow & blue phase. - Ketatka skru TOP DEMAND CABLE CONNECTION - Check amps, voltage & phase rotation - Normalise | [7 empty] | 19 | TRUE
343 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01011 | CHERAS BARU NO. 2 | OUTGOING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F1 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-05 | 2023-07-05 | 2023-07-05 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 8 | TRUE
344 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01011 | CHERAS BARU NO. 2 | OUTGOING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F1 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-05 | 2023-07-05 | 2023-07-05 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 8 | TRUE
345 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01011 | CHERAS BARU NO. 2 | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F4 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-05 | 2023-07-05 | 2023-07-05 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 8 | TRUE
346 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | 25 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01011 | CHERAS BARU NO. 2 | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F5 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-05 | 2023-07-05 | 2023-07-05 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 8 | TRUE
347 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | 7 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01011 | CHERAS BARU NO. 2 | OUTGOING 6 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F5 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-05 | 2023-07-05 | 2023-07-05 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 8 | TRUE
348 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | 18 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01011 | CHERAS BARU NO. 2 | OUTGOING 7 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F7 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-05 | 2023-07-05 | 2023-07-05 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 8 | TRUE
349 | 2023-06-27 | INFRAKOMAS | THERMOGRAPHY |  | 19 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01011 | CHERAS BARU NO. 2 | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F8 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-05 | 2023-07-05 | 2023-07-05 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 8 | TRUE
350 | 2023-06-28 | INFRAKOMAS | THERMOGRAPHY |  | 18 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01066 | PE TMN CHERAS NO.3 | OUTGOING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F1 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-07 | 2023-07-07 | 2023-07-07 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
351 | 2023-06-28 | INFRAKOMAS | THERMOGRAPHY |  | 8 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00752 | PE TMN SRI BAHAGIA NO.3 | INCOMING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP (TX 1): INCOMING 1 - RED PHASE LINK | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-16 | 2023-07-16 | FUSE / LINK | CLEANING | Action Taken - Gosok dan ketatkan skru link incoming red & blue phase link - Tambah baru link incoming 1 untuk red, yellow & blue phase - Check amps, voltage & phase rotation - Normalise | [7 empty] | 18 | TRUE
352 | 2023-06-28 | INFRAKOMAS | THERMOGRAPHY |  | 9 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00752 | PE TMN SRI BAHAGIA NO.3 | INCOMING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP (TX 1): INCOMING 1 - BLUE PHASE LINK | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-16 | 2023-07-16 | FUSE / LINK | CLEANING | Action Taken - Gosok dan ketatkan skru link incoming red & blue phase link - Tambah baru link incoming 1 untuk red, yellow & blue phase - Check amps, voltage & phase rotation - Normalise | [7 empty] | 18 | TRUE
353 | 2023-06-28 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00752 | PE TMN SRI BAHAGIA NO.3 | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP (TX 1): OUTGOING F5 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-07 | 2023-07-07 | 2023-07-07 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
354 | 2023-06-28 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00752 | PE TMN SRI BAHAGIA NO.3 | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP (TX 1): OUTGOING F5 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-07 | 2023-07-07 | 2023-07-07 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
355 | 2023-06-28 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00752 | PE TMN SRI BAHAGIA NO.3 | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP (TX 1): OUTGOING F5 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-07 | 2023-07-07 | 2023-07-07 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
356 | 2023-06-28 | INFRAKOMAS | THERMOGRAPHY |  | 22 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00060 | PE DESA TUN RAZAK NO.1 | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F2 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-07 | 2023-07-07 | 2023-07-07 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
357 | 2023-06-28 | INFRAKOMAS | THERMOGRAPHY |  | 14 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | EWT | XLPE | WKLS/PCE/J00379 | PE SALAK SOUTH GARDEN NO.5 | OUTGOING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F1 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-07 | 2023-07-07 | 2023-07-07 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
358 | 2023-06-28 | INFRAKOMAS | THERMOGRAPHY |  | 30 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | EWT | XLPE | WKLS/PCE/J00379 | PE SALAK SOUTH GARDEN NO.5 | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F4 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-07 | 2023-07-07 | 2023-07-07 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
359 | 2023-06-28 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | EWT | XLPE | WKLS/PCE/J00379 | PE SALAK SOUTH GARDEN NO.5 | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F4 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-07 | 2023-07-07 | 2023-07-07 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
360 | 2023-06-28 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | EWT | XLPE | WKLS/PCE/J00379 | PE SALAK SOUTH GARDEN NO.5 | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F4 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-07 | 2023-07-07 | 2023-07-07 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
361 | 2023-06-28 | INFRAKOMAS | THERMOGRAPHY |  | 33 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | EWT | XLPE | WKLS/PCE/J00379 | PE SALAK SOUTH GARDEN NO.5 | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F5 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-07 | 2023-07-07 | 2023-07-07 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
362 | 2023-06-28 | INFRAKOMAS | THERMOGRAPHY |  | 27 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | EWT | XLPE | WKLS/PCE/J00379 | PE SALAK SOUTH GARDEN NO.5 | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F5 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-07 | 2023-07-07 | 2023-07-07 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
363 | 2023-06-28 | INFRAKOMAS | THERMOGRAPHY |  | 15 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | EWT | XLPE | WKLS/PCE/J00379 | PE SALAK SOUTH GARDEN NO.5 | OUTGOING 6 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP: OUTGOING F6 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-07 | 2023-07-07 | 2023-07-07 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
364 | 2023-06-28 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | PILC | WKLS/PCE/J00368 | PE SALAK SOUTH GARDEN NO.4 | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB: OUTGOING F4 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-07 | 2023-07-07 | 2023-07-07 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
365 | 2023-06-28 | INFRAKOMAS | THERMOGRAPHY |  | 33 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | PILC | WKLS/PCE/J00368 | PE SALAK SOUTH GARDEN NO.4 | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB: OUTGOING F4 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-07 | 2023-07-07 | 2023-07-07 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
366 | 2023-06-28 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | PILC | WKLS/PCE/J00368 | PE SALAK SOUTH GARDEN NO.4 | OUTGOING 6 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB: OUTGOING F6 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-07 | 2023-07-07 | 2023-07-07 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
367 | 2023-07-04 | INFRAKOMAS | THERMOGRAPHY |  | 37 | LVDB / F.PILLAR | RMU MOTORIZED | EPE | MTM | PILC | WKLS/PCE/J00378 | SRI PETALING ZON L | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F2 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-13 | 2023-07-13 | 2023-07-13 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
368 | 2023-07-04 | INFRAKOMAS | THERMOGRAPHY |  | 29 | LVDB / F.PILLAR | RMU MOTORIZED | EPE | MTM | XLPE | WKLS/PCE/J00378 | SRI PETALING ZON L | OUTGOING 3 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F3 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-13 | 2023-07-13 | 2023-07-13 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
369 | 2023-07-04 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU MOTORIZED | EPE | MTM | PILC | WKLS/PCE/J00378 | SRI PETALING ZON L | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F5 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-13 | 2023-07-13 | 2023-07-13 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
370 | 2023-07-04 | INFRAKOMAS | THERMOGRAPHY |  | 43 | LVDB / F.PILLAR | RMU MOTORIZED | EPE | MTM | XLPE | WKLS/PCE/J00378 | SRI PETALING ZON L | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F8 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-13 | 2023-07-13 | 2023-07-13 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
371 | 2023-07-04 | INFRAKOMAS | THERMOGRAPHY |  | 6 | TRANSFORMER | VCB | TAMCO | EWT | XLPE | WKLS/PCE/J00206 | SRI PETALING ZON F NO. 2 | TX1 | HOTSPOT | TX BUSHING | HOTSPOT AT TX: HV SIDE - RED PHASE BUSHING | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-30 | 2023-07-30 | TX HV BUSHING | TIGHTNESS INSPECTION | [8 empty] | 26 | TRUE
372 | 2023-07-05 | INFRAKOMAS | THERMOGRAPHY |  | 25 | LVDB / F.PILLAR | VCB | TOSHIBA | SGB | XLPE | WKLS/PCE/J00201 | KEDAI/PEJ JLN RADEN ANUM SRI PETALING | OUTGOING 4 | HOTSPOT | EARTHING | HOTSPOT AT LVDB: OUTGOING F4 - EARTHING CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-10 | 2023-07-10 | 2023-07-10 | EARTHING | TIGHTNESS INSPECTION | KETATKAN SAMBUNGAN EARTHING | [7 empty] | 5 | TRUE
373 | 2023-07-05 | INFRAKOMAS | THERMOGRAPHY |  | 23 | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00147 | LOT BANGLO TMN BILLION CHERAS | INCOMING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): INCOMING 1 - RED PHASE LINK | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-21 | 2023-07-21 | FUSE / LINK | CLEANING | Action Taken - Gosok dan ketatkan skru dan nut link incoming 1 - Tambah link incoming 2 - Check amps, voltage & phase rotation - Normalise | [7 empty] | 16 | TRUE
374 | 2023-07-05 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00182 | JLN 4/146 BDR TASIK SELATAN | OUTGOING 3 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F3 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-10 | 2023-07-10 | 2023-07-10 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 5 | TRUE
375 | 2023-07-05 | INFRAKOMAS | THERMOGRAPHY |  | 12 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00182 | JLN 4/146 BDR TASIK SELATAN | INCOMING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): INCOMING 2 - YELLOW PHASE LINK | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-30 | 2023-07-30 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 25 | TRUE
376 | 2023-07-05 | INFRAKOMAS | THERMOGRAPHY |  | 33 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00005 | JLN 8/146 NO. 2 BDR TASIK SELATAN | OUTGOING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F1 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-10 | 2023-07-10 | 2023-07-10 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 5 | TRUE
377 | 2023-07-05 | INFRAKOMAS | THERMOGRAPHY |  | 27 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | XLPE | WKLS/PCE/J00195 | JLN 8/146 NO. 1 BDR TASIK SELATAN | OUTGOING 7 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F7 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-07-10 | 2023-07-10 | 2023-07-10 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 5 | TRUE
378 | 2023-07-06 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00227 | FLAT DBKL JLN BUDIMAN 1 BDR TAR | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F5 - RED PHASE FUSE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-05 | 2023-08-05 | 2023-08-05 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 30 | TRUE
379 | 2023-07-06 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00227 | FLAT DBKL JLN BUDIMAN 1 BDR TAR | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F5 - YELLOW PHASE FUSE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-05 | 2023-08-05 | 2023-08-05 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 30 | TRUE
380 | 2023-07-06 | INFRAKOMAS | THERMOGRAPHY |  |  | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00227 | FLAT DBKL JLN BUDIMAN 1 BDR TAR | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F5 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-05 | 2023-08-05 | 2023-08-05 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 30 | TRUE
381 | 2023-07-06 | INFRAKOMAS | THERMOGRAPHY |  | 28 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01062 | TMN CHERAS INDAH NO. 1 | INCOMING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): INCOMING 1 - BLUE PHASE LINK (BOLT & NUT) | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-31 | 2023-07-31 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 25 | TRUE
382 | 2023-07-06 | INFRAKOMAS | THERMOGRAPHY |  | 27 | LVDB / F.PILLAR | RMU SF6 | SCHNEIDER | EWT | XLPE | WKLS/PCE/J00561 | PDT LOJI IWK JLN 13/91 | OUTGOING 3 | HOTSPOT | CABLE LUG / TERMINATION | HOTSPOT AT LVFP: OUTGOING F3 - YELLOW PHASE CABLE CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-10-06 | 2023-10-06 | 2023-10-06 | FUSE / LINK | REPLACEMENT | TUKAR KABEL LUG BARU | [7 empty] | 92 | TRUE
383 | 2023-07-06 | INFRAKOMAS | THERMOGRAPHY |  | 30 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01098 | TMN SHAMELIN PERKASA NO. 20 | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 2): OUTGOING F5 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-05 | 2023-08-05 | 2023-08-05 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 30 | TRUE
384 | 2023-07-07 | INFRAKOMAS | THERMOGRAPHY |  | 28 | LVDB / F.PILLAR | VCB | EPE | MTM | PILC | WKLS/PCE/J01099 | TMN SHAMELIN PERKASA NO. 21 | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F5 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-05 | 2023-08-05 | 2023-08-05 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 29 | TRUE
385 | 2023-07-07 | INFRAKOMAS | THERMOGRAPHY |  | 22 | LVDB / F.PILLAR | VCB | EPE | MTM | PILC | WKLS/PCE/J01099 | TMN SHAMELIN PERKASA NO. 21 | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB (TX 1): OUTGOING F8 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-05 | 2023-08-05 | 2023-08-05 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 29 | TRUE
386 | 2023-07-07 | INFRAKOMAS | THERMOGRAPHY |  | 21 | LVDB / F.PILLAR | VCB | EPE | MTM | XLPE | WKLS/PCE/J01099 | TMN SHAMELIN PERKASA NO. 21 | OUTGOING 3 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVFP (TX 2): OUTGOING F3 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-05 | 2023-08-05 | 2023-08-05 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 29 | TRUE
387 | 2023-07-07 | INFRAKOMAS | THERMOGRAPHY |  | 44 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J00398 | BALAI POLIS SALAK SOUTH N/VILLAGE | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB: OUTGOING F5 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-05 | 2023-08-05 | 2023-08-05 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 29 | TRUE
388 | 2023-07-10 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00354 | KG MALAYSIA TAMBAHAN | OUTGOING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB: OUTGOING F1 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-04 | 2023-08-04 | 2023-08-04 | FUSE / LINK | REPLACEMENT | [8 empty] | 25 | TRUE
389 | 2023-07-10 | INFRAKOMAS | THERMOGRAPHY |  | 33 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00354 | KG MALAYSIA TAMBAHAN | OUTGOING 3 | HOTSPOT | CABLE LUG / TERMINATION | HOTSPOT AT LVDB: OUTGOING F3 - RED PHASE CABLE LUG | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-04 | 2023-08-04 | 2023-08-04 | LUG | REPLACEMENT | TUKAR CABLE LUG BARU | [7 empty] | 25 | TRUE
390 | 2023-07-10 | INFRAKOMAS | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00354 | KG MALAYSIA TAMBAHAN | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB: OUTGOING F8 - RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-04 | 2023-08-04 | 2023-08-04 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 25 | TRUE
391 | 2023-07-11 | INFRAKOMAS | THERMOGRAPHY |  | 20 | LVDB / F.PILLAR | VCB | TAMCO | EWT | XLPE | WKLS/PCE/J00417 | RODA INDAH | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB: OUTGOING F2 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-02 | 2023-08-02 | 2023-08-02 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 22 | TRUE
392 | 2023-07-11 | INFRAKOMAS | THERMOGRAPHY |  | 24 | LVDB / F.PILLAR | VCB | TAMCO | EWT | PILC | WKLS/PCE/J00417 | RODA INDAH | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB: OUTGOING F5 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-02 | 2023-08-02 | 2023-08-02 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 22 | TRUE
393 | 2023-07-11 | INFRAKOMAS | THERMOGRAPHY |  | 13 | LVDB / F.PILLAR | VCB | TAMCO | EWT | PILC | WKLS/PCE/J00417 | RODA INDAH | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB: OUTGOING F5 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-02 | 2023-08-02 | 2023-08-02 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 22 | TRUE
394 | 2023-07-11 | INFRAKOMAS | THERMOGRAPHY |  | 22 | LVDB / F.PILLAR | VCB | TAMCO | EWT | XLPE | WKLS/PCE/J00417 | RODA INDAH | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB: OUTGOING F8 - YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-02 | 2023-08-02 | 2023-08-02 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 22 | TRUE
395 | 2023-07-11 | INFRAKOMAS | THERMOGRAPHY |  | 29 | LVDB / F.PILLAR | VCB | TAMCO | EWT | XLPE | WKLS/PCE/J00417 | RODA INDAH | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB: OUTGOING F8 - BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-02 | 2023-08-02 | 2023-08-02 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 22 | TRUE
396 | 2023-07-12 | INFRAKOMAS | THERMOGRAPHY |  | 17 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00266 | TMN ANGKASA | INCOMING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT LVDB: INCOMING 2 - BLUE PHASE LINK | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-07-31 | 2023-07-31 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 19 | TRUE
397 | 2023-07-17 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 20 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J00797 | TRANSIT QUARTERS PANTAI DALAM | OUTGOING 1 | HOTSPOT | CABLE LUG / TERMINATION | OUTGOING F1: BLUE PHASE CABLE LUG CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-10-12 | 2023-10-12 | 2023-10-12 | LUG | REPLACEMENT | TUKAR BIMETAL BARU | [7 empty] | 87 | TRUE
398 | 2023-07-22 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 24 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | PILC | WKLS/PCE/J00487 | CHOO MUN SANG | OUTGOING 1 | HOTSPOT | FUSE / LINK | OUTGOING F1: RED PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-01 | 2023-08-01 | 2023-08-01 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 10 | TRUE
399 | 2023-07-23 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 41 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00486 | FORESIGHT TRADING | OUTGOING 3 | HOTSPOT | FUSE / LINK | OUTGOING F3: RED PHASE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-01 | 2023-08-01 | 2023-08-01 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 9 | TRUE
400 | 2023-07-23 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 50 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00486 | FORESIGHT TRADING | OUTGOING 3 | HOTSPOT | FUSE / LINK | OUTGOING F3: YELLOW PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-01 | 2023-08-01 | 2023-08-01 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 9 | TRUE
401 | 2023-07-24 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 7 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM |  |  | WKLS/PCE/J00741 | TMN DELIMA | INCOMING 1 | HOTSPOT | FUSE / LINK | INCOMING 1: RED PHASE LINK CONNECTION | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-03 | 2023-09-03 | FUSE / LINK | CLEANING | [8 empty] | 41 | TRUE
402 | 2023-07-24 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 11 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM |  |  | WKLS/PCE/J00741 | TMN DELIMA | INCOMING 1 | HOTSPOT | FUSE / LINK | INCOMING 1: YELLOW PHASE LINK CONNECTION | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-03 | 2023-09-03 | FUSE / LINK | CLEANING | [8 empty] | 41 | TRUE
403 | 2023-07-24 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 9 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM |  |  | WKLS/PCE/J00741 | TMN DELIMA | INCOMING 2 | HOTSPOT | FUSE / LINK | INCOMING 2: RED PHASE LINK CONNECTION | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-03 | 2023-09-03 | FUSE / LINK | CLEANING | [8 empty] | 41 | TRUE
404 | 2023-07-24 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 13 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM |  |  | WKLS/PCE/J00741 | TMN DELIMA | INCOMING 2 | HOTSPOT | FUSE / LINK | INCOMING 2: YELLOW PHASE LINK CONNECTION | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-03 | 2023-09-03 | FUSE / LINK | CLEANING | [8 empty] | 41 | TRUE
405 | 2023-07-24 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 22 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM |  |  | WKLS/PCE/J00741 | TMN DELIMA | INCOMING 2 | HOTSPOT | FUSE / LINK | INCOMING 2: BLUE PHASE LINK CONNECTION | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-03 | 2023-09-03 | FUSE / LINK | CLEANING | [8 empty] | 41 | TRUE
406 | 2023-07-24 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 5 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM |  | XLPE | WKLS/PCE/J00741 | TMN DELIMA | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING F6: RED PHASE FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-03 | 2023-08-03 | 2023-08-03 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 10 | TRUE
407 | 2023-07-24 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 10 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM |  | XLPE | WKLS/PCE/J00741 | TMN DELIMA | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING F6: YELLOW PHASE FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-03 | 2023-08-03 | 2023-08-03 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 10 | TRUE
408 | 2023-07-24 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 27 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM |  | XLPE | WKLS/PCE/J00741 | TMN DELIMA | OUTGOING 6 | HOTSPOT | FUSE / LINK | OUTGOING F6: BLUE PHASE FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-03 | 2023-08-03 | 2023-08-03 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 10 | TRUE
409 | 2023-07-24 | EET ENGINEERING SERVICES | ULTRASOUND | 8 |  | SWITCHGEAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00229 | JLN DAMAI PERDANA 1/4 BDR DAMAI PERDANA | TX PANEL | CORONA DISCHARGE | BREAKER COMPARTMENT | CORONA AT PANEL 43987, TX 2 | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-10-02 | 2023-10-02 | VCB | SERVICING (CB ONLY) | Action Taken - Preventive Maintenance suisgear VCB Tamco Scada-Ready 2+2 - Preventive Maintenance TX hermatically Sealed 1000KVA - Maintenance EFI Emg 2nos - Maintenance Battery Charger - Tutup lubang cable menggunakan fibre plate dan silkcon - Check amps, voltage dan phase rotation - Normalise | [7 empty] | 70 | TRUE
410 | 2023-07-24 | EET ENGINEERING SERVICES | ULTRASOUND | 12 |  | SWITCHGEAR | VCB | TAMCO | MTM |  | WKLS/PCE/J00229 | JLN DAMAI PERDANA 1/4 BDR DAMAI PERDANA | 11KV CABLE FEEDER | CORONA DISCHARGE | BREAKER COMPARTMENT | CORONA AT PANEL 18274, JLN DAMAI PERDANA 1/3 DAMAI PERDANA | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-10-02 | 2023-10-02 | VCB | SERVICING (CB ONLY) | Action Taken - Preventive Maintenance suisgear VCB Tamco Scada-Ready 2+2 - Preventive Maintenance TX hermatically Sealed 1000KVA - Maintenance EFI Emg 2nos - Maintenance Battery Charger - Tutup lubang cable menggunakan fibre plate dan silkcon - Check amps, voltage dan phase rotation - Normalise | [7 empty] | 70 | TRUE
411 | 2023-07-24 | EET ENGINEERING SERVICES | ULTRASOUND | 18 |  | SWITCHGEAR | VCB | TAMCO | MTM |  | WKLS/PCE/J00229 | JLN DAMAI PERDANA 1/4 BDR DAMAI PERDANA | 11KV CABLE FEEDER | TRACKING SOUND | BREAKER COMPARTMENT | TRACKING AT PANEL 18272, JLN DAMAI PERDANA 3/1J DAMAI PERDANA | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-10-02 | 2023-10-02 | VCB | SERVICING (CB ONLY) | Action Taken - Preventive Maintenance suisgear VCB Tamco Scada-Ready 2+2 - Preventive Maintenance TX hermatically Sealed 1000KVA - Maintenance EFI Emg 2nos - Maintenance Battery Charger - Tutup lubang cable menggunakan fibre plate dan silkcon - Check amps, voltage dan phase rotation - Normalise | [7 empty] | 70 | TRUE
412 | 2023-07-24 | EET ENGINEERING SERVICES | ULTRASOUND | 10 |  | SWITCHGEAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00229 | JLN DAMAI PERDANA 1/4 BDR DAMAI PERDANA | TX PANEL | CORONA DISCHARGE | BREAKER COMPARTMENT | CORONA AT PANEL 18273, TX 1 | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-10-02 | 2023-10-02 | VCB | SERVICING (CB ONLY) | Action Taken - Preventive Maintenance suisgear VCB Tamco Scada-Ready 2+2 - Preventive Maintenance TX hermatically Sealed 1000KVA - Maintenance EFI Emg 2nos - Maintenance Battery Charger - Tutup lubang cable menggunakan fibre plate dan silkcon - Check amps, voltage dan phase rotation - Normalise | [7 empty] | 70 | TRUE
413 | 2023-07-24 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 14 | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00229 | JLN DAMAI PERDANA 1/4 BDR DAMAI PERDANA | OUTGOING 6 | HOTSPOT | CABLE LUG / TERMINATION | OUTGOING F6: RED PHASE CABLE LUG CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-10-18 | 2023-10-18 | 2023-10-18 | LUG | REPLACEMENT | TUKAR BIMETAL BARU | [7 empty] | 86 | TRUE
414 | 2023-07-24 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | SGB | XLPE | WKLS/PCE/J00559 | JLN DAMAI PERDANA 1 BDR DAMAI PERDANA | OUTGOING 3 | HOTSPOT | FUSE / LINK | OUTGOING F3: YELLOW PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-03 | 2023-08-03 | 2023-08-03 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 10 | TRUE
415 | 2023-07-26 | EET ENGINEERING SERVICES | ULTRASOUND | 8 |  | SWITCHGEAR | VCB | LKH HSS | MTM |  | WKLS/PCE/J00056 | JLN DAMAI PERDANA 4/1F BDR DAMAI PERDANA | TX PANEL | CORONA DISCHARGE | CABLE COMPARTMENT | CORONA AT PANEL 18270, TX | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-10-03 | 2023-10-03 | VCB | SERVICING (CB ONLY) | [8 empty] | 69 | TRUE
416 | 2023-07-26 | EET ENGINEERING SERVICES | ULTRASOUND | 4 |  | SWITCHGEAR | VCB | LKH HSS | MTM |  | WKLS/PCE/J00056 | JLN DAMAI PERDANA 4/1F BDR DAMAI PERDANA | 11KV CABLE FEEDER | CORONA DISCHARGE | CABLE COMPARTMENT | CORONA AT PANEL 18271, PE D'SQUARE 1 JDP 6/1C | REPAIR IMMEDIATELY | CABLE MAINTENANCE |  | 2023-09-30 | 2023-08-14 | TERMINATION | NEW TERMINATION | Details : Termination dalam keadaan baik. Suis gear Vcb LKH, saiz kabel 240mmp xlpe. Buat termination baru. Kerja siap dan normalised. | [7 empty] | 19 | TRUE
417 | 2023-07-27 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 17 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00452 | JLN DAMAI RASA 1 ALAM DAMAI | OUTGOING 2 | HOTSPOT | FUSE / LINK | LV BOARD TX1: OUTGOING F2 - RED PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-14 | 2023-08-14 | 2023-08-14 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 18 | TRUE
418 | 2023-07-27 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00253 | DESA TUN RAZAK B | OUTGOING 1 | HOTSPOT | FUSE / LINK | F/PILLAR (TX2): OUTGOING F1 - BLUE PHASE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-03 | 2023-08-03 | 2023-08-03 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 7 | TRUE
419 | 2023-07-27 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 20 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00251 | DESA TUN RAZAK A | OUTGOING 5 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F5 - YELLOW PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-14 | 2023-08-14 | 2023-08-14 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 18 | TRUE
420 | 2023-07-27 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 35 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00251 | DESA TUN RAZAK A | OUTGOING 5 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F5 - BLUE PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-14 | 2023-08-14 | 2023-08-14 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 18 | TRUE
421 | 2023-07-27 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 36 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00251 | DESA TUN RAZAK A | OUTGOING 1 | HOTSPOT | FUSE / LINK | F/PILLAR (TX2): OUTGOING F1 - YELLOW PASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-14 | 2023-08-14 | 2023-08-14 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 18 | TRUE
422 | 2023-07-27 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 24 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | PILC | WKLS/PCE/J00251 | DESA TUN RAZAK A | OUTGOING 2 | HOTSPOT | FUSE / LINK | F/PILLAR (TX2): OUTGOING F2 - RED PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-14 | 2023-08-14 | 2023-08-14 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 18 | TRUE
423 | 2023-07-27 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 32 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00251 | DESA TUN RAZAK A | OUTGOING 7 | HOTSPOT | FUSE / LINK | F/PILLAR (TX2): OUTGOING F7 - BLUE PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-14 | 2023-08-14 | 2023-08-14 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 18 | TRUE
424 | 2023-07-29 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 15 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | EWT | PILC | WKLS/PCE/J00774 | TMN SRI SENTOSA NO. 3 | OUTGOING 2 | HOTSPOT | CABLE LUG / TERMINATION | LV BOARD (TX1): OUTGOING F2 - NEUTRAL CABLE LUG CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-10 | 2023-08-10 | 2023-08-10 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 12 | TRUE
425 | 2023-07-29 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 48 | LVDB / F.PILLAR | RMU SF6 | SIEMENS | EWT | XLPE | WKLS/PCE/J00773 | TMN SRI SENTOSA NO. 4 | OUTGOING 6 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F6 - YELLOW PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-10 | 2023-08-10 | 2023-08-10 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 12 | TRUE
426 | 2023-07-29 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 23 | LVDB / F.PILLAR | RMU SF6 | SIEMENS | EWT | XLPE | WKLS/PCE/J00773 | TMN SRI SENTOSA NO. 4 | OUTGOING 7 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F7 - RED PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-10 | 2023-08-10 | 2023-08-10 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 12 | TRUE
427 | 2023-07-29 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 29 | LVDB / F.PILLAR | RMU SF6 | SIEMENS | EWT | XLPE | WKLS/PCE/J00773 | TMN SRI SENTOSA NO. 4 | OUTGOING 7 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F7 - BLUE PHASE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-10 | 2023-08-10 | 2023-08-10 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 12 | TRUE
428 | 2023-08-01 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TOSHIBA | EWT | XLPE | WKLS/PCE/J00511 | DAH YUNG STEEL | OUTGOING 4 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F4 - RED PHASE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-12 | 2023-08-12 | 2023-08-12 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 11 | TRUE
429 | 2023-08-01 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | PILC | WKLS/PCE/J00512 | CHEONG FOUNDARY | OUTGOING 1 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F1 - RED PHASE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-12 | 2023-08-12 | 2023-08-12 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 11 | TRUE
430 | 2023-08-01 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 30 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | PILC | WKLS/PCE/J00512 | CHEONG FOUNDARY | OUTGOING 1 | HOTSPOT | CABLE LUG / TERMINATION | LV BOARD (TX1): OUTGOING F1 - BLUE PHASE CABLE LUG CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-12 | 2023-08-12 | 2023-08-12 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 11 | TRUE
431 | 2023-08-01 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU MOTORIZED | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00512 | CHEONG FOUNDARY | OUTGOING 3 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F3 - YELLOW PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-12 | 2023-08-12 | 2023-08-12 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 11 | TRUE
432 | 2023-08-02 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 25 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM |  |  | WKLS/PCE/J00536 | MALAYAN TOBACCO | OUTGOING 4 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F4 - RED PHASE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-12 | 2023-08-12 | 2023-08-12 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 10 | TRUE
433 | 2023-08-02 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 23 | LVDB / F.PILLAR | VCB | TAMCO | EWT |  | WKLS/PCE/J00535 | JLN TIGA | OUTGOING 6 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F6 - YELLOW PHASE FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-12 | 2023-08-12 | 2023-08-12 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 10 | TRUE
434 | 2023-08-02 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TAMCO | EWT |  | WKLS/PCE/J00535 | JLN TIGA | OUTGOING 6 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F6 - BLUE PHASE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-12 | 2023-08-12 | 2023-08-12 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 10 | TRUE
435 | 2023-08-02 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TAMCO | EWT |  | WKLS/PCE/J00535 | JLN TIGA | OUTGOING 7 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F7 - RED PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-12 | 2023-08-12 | 2023-08-12 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 10 | TRUE
436 | 2023-08-02 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 30 | LVDB / F.PILLAR | VCB | TAMCO | EWT |  | WKLS/PCE/J00535 | JLN TIGA | OUTGOING 7 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F7 - BLUE PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-12 | 2023-08-12 | 2023-08-12 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 10 | TRUE
437 | 2023-08-03 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00472 | HIN FATT | OUTGOING 8 | HOTSPOT | FUSE / LINK | F/PILLAR (TX1): OUTGOING F8 - YELLOW PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-12 | 2023-08-12 | 2023-08-12 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 9 | TRUE
438 | 2023-08-03 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 28 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | XLPE | WKLS/PCE/J00542 | WISMA NCK | OUTGOING 5 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F5 - RED PAHSE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-16 | 2023-08-16 | 2023-08-16 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 13 | TRUE
439 | 2023-08-03 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | XLPE | WKLS/PCE/J00542 | WISMA NCK | OUTGOING 5 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F5 - BLUE PAHSE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-16 | 2023-08-16 | 2023-08-16 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 13 | TRUE
440 | 2023-08-03 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 21 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00541 | KFC WP | OUTGOING 2 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F2 - YELLOW PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-16 | 2023-08-16 | 2023-08-16 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 13 | TRUE
441 | 2023-08-03 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00541 | KFC WP | OUTGOING 2 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F2 - BLUE PAHSE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-16 | 2023-08-16 | 2023-08-16 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 13 | TRUE
442 | 2023-08-04 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 47 | LVDB / F.PILLAR | VCB | LKH HSS | MTM | XLPE | WKLS/PCE/J00078 | PASAR RAYA WARTA | OUTGOING 8 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F8 - RED PAHSE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-21 | 2023-09-21 | 2023-09-21 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 48 | TRUE
443 | 2023-08-04 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 13 | LVDB / F.PILLAR | RMU SF6 | TAMCO | EWT | XLPE | WKLS/PCE/J00909 | 24 KLG TERES 1 TKT SG BESI | OUTGOING 4 | HOTSPOT | FUSE / LINK | LV BOARD (TX2): OUTGOING F4 - RED PAHSE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-21 | 2023-09-21 | 2023-09-21 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 48 | TRUE
444 | 2023-08-15 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 38 | LVDB / F.PILLAR | VCB | EPE | MTM | XLPE | WKLS/PCE/J00903 | TMN ABADI INDAH JLN 2/109C | OUTGOING 4 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F4 - YELLOW PHASE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-29 | 2023-08-29 | 2023-08-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 14 | TRUE
445 | 2023-08-15 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01217 | KUCHAI EXCHANGE NO. 2 | OUTGOING 4 | HOTSPOT | FUSE / LINK | F/PILLAR (TX1): OUTGOING F4 - RED PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-29 | 2023-08-29 | 2023-08-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 14 | TRUE
446 | 2023-08-16 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 50 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00693 | TMN MIDAH FACTORY NO. 2 | OUTGOING 8 | HOTSPOT | FUSE / LINK | LV BOARD (TX 2): OUTGOING F4 - RED PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-31 | 2023-08-31 | 2023-08-31 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 15 | TRUE
447 | 2023-08-16 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 5 | TRANSFORMER | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00248 | PDT LUCKY CREAMERY | TX1 | HOTSPOT | TX BUSHING | TX 1: LV-SIDE - RED PHASE BUSHING CONNECTION | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-05 | 2023-09-05 | TX LV BUSHING | TIGHTNESS INSPECTION | [8 empty] | 20 | TRUE
448 | 2023-08-16 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00248 | PDT LUCKY CREAMERY | OUTGOING 2 | HOTSPOT | FUSE / LINK | LV BOARD: OUTGOING F2 - RED PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-30 | 2023-08-30 | 2023-08-30 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 14 | TRUE
449 | 2023-08-16 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00248 | PDT LUCKY CREAMERY | OUTGOING 4 | HOTSPOT | FUSE / LINK | LV BOARD: OUTGOING F4 - BLUE PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-30 | 2023-08-30 | 2023-08-30 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 14 | TRUE
450 | 2023-08-16 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 29 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00694 | TMN MIDAH FACTORY NO. 3 | OUTGOING 2 | HOTSPOT | FUSE / LINK | LV BOARD (TX 2): OUTGOING F2 - BLUE PHASE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-09 | 2023-09-09 | 2023-09-09 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 24 | TRUE
451 | 2023-08-16 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 24 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00694 | TMN MIDAH FACTORY NO. 3 | OUTGOING 4 | HOTSPOT | FUSE / LINK | LV BOARD (TX 2): OUTGOING F4 - YELLOW PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-09 | 2023-09-09 | 2023-09-09 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 24 | TRUE
452 | 2023-08-16 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 23 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | PILC | WKLS/PCE/J00691 | TMN MIDAH NO. 4 | OUTGOING 2 | HOTSPOT | FUSE / LINK | LV BOARD (TX1): OUTGOING F2 - BLUE PHASE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-31 | 2023-08-31 | 2023-08-31 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 15 | TRUE
453 | 2023-08-16 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 15 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | SGB | XLPE | WKLS/PCE/J00691 | TMN MIDAH NO. 4 | INCOMING 2 | HOTSPOT | FUSE / LINK | F/PILLAR (TX2): INCOMING 2 - BLUE PHASE CABLE LUG CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-31 | 2023-08-31 | 2023-08-31 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 15 | TRUE
454 | 2023-08-17 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00115 | SRJK(C) CONFUCIAN JLN SG BESI | OUTGOING 5 | HOTSPOT | FUSE / LINK | LV BOARD: OUTGOING F5 - YELLOW PHASE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-29 | 2023-08-29 | 2023-08-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 12 | TRUE
455 | 2023-08-17 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00115 | SRJK(C) CONFUCIAN JLN SG BESI | OUTGOING 5 | HOTSPOT | FUSE / LINK | LV BOARD: OUTGOING F5 - BLUE PHASE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-29 | 2023-08-29 | 2023-08-29 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 12 | TRUE
456 | 2023-08-17 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 1 | SWITCHGEAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00117 | KILANG BERKEMBAR JLN SHAMELIN NIAGA1 | TX PANEL | HOTSPOT | CABLE COMPARTMENT | PANEL 39370 TX 2 1000 KVA - FUSE COMPARTMENT | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-05 | 2023-09-05 | RMU | TIGHTNESS INSPECTION | [8 empty] | 19 | TRUE
457 | 2023-08-17 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00117 | KILANG BERKEMBAR JLN SHAMELIN NIAGA1 | OUTGOING 8 | HOTSPOT | FUSE / LINK | LV BOARD (TX2): OUTGOING F8 - BLUE PHASE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-31 | 2023-08-31 | 2023-08-31 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 14 | TRUE
458 | 2023-08-17 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 10 | LVDB / F.PILLAR | RMU SF6 | ABB | MTM | XLPE | WKLS/PCE/J00680 | TMN MIDAH NO 1 | OUTGOING 6 | HOTSPOT | FUSE / LINK | F/PILLAR (TX1): OUTGOING F6 - RED PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-31 | 2023-08-31 | 2023-08-31 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 14 | TRUE
459 | 2023-08-17 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 24 | LVDB / F.PILLAR | RMU SF6 | ABB | MTM | XLPE | WKLS/PCE/J00680 | TMN MIDAH NO 1 | OUTGOING 6 | HOTSPOT | FUSE / LINK | F/PILLAR (TX1): OUTGOING F6 - YELLOW PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-31 | 2023-08-31 | 2023-08-31 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 14 | TRUE
460 | 2023-08-17 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 15 | LVDB / F.PILLAR | RMU SF6 | ABB | MTM | XLPE | WKLS/PCE/J00680 | TMN MIDAH NO 1 | OUTGOING 1 | HOTSPOT | FUSE / LINK | F/PILLAR (TX2): OUTGOING F1 - RED PHASE CABLE LUG CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-31 | 2023-08-31 | 2023-08-31 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 14 | TRUE
461 | 2023-08-17 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | ABB | MTM | XLPE | WKLS/PCE/J00680 | TMN MIDAH NO 1 | OUTGOING 4 | HOTSPOT | FUSE / LINK | F/PILLAR (TX2): OUTGOING F4 - RED PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-31 | 2023-08-31 | 2023-08-31 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 14 | TRUE
462 | 2023-08-17 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | ABB | MTM | XLPE | WKLS/PCE/J00680 | TMN MIDAH NO 1 | OUTGOING 5 | HOTSPOT | FUSE / LINK | F/PILLAR (TX2): OUTGOING F5 - RED PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-31 | 2023-08-31 | 2023-08-31 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 14 | TRUE
463 | 2023-08-17 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | ABB | MTM | XLPE | WKLS/PCE/J00680 | TMN MIDAH NO 1 | OUTGOING 5 | HOTSPOT | FUSE / LINK | F/PILLAR (TX2): OUTGOING F5 - BLUE PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-31 | 2023-08-31 | 2023-08-31 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 14 | TRUE
464 | 2023-08-17 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 13 | LVDB / F.PILLAR | RMU SF6 | SCHNEIDER | EWT | XLPE | WKLS/PCE/J01520 | PADAT TAMAN MIDAH NO 1 | OUTGOING 6 | HOTSPOT | FUSE / LINK | LV BOARD: OUTGOING F6 - RED PHASE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-31 | 2023-08-31 | 2023-08-31 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 14 | TRUE
465 | 2023-08-17 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 19 | LVDB / F.PILLAR | RMU SF6 | SCHNEIDER | EWT | XLPE | WKLS/PCE/J01520 | PADAT TAMAN MIDAH NO 1 | OUTGOING 6 | HOTSPOT | FUSE / LINK | LV BOARD: OUTGOING F6 - YELLOW PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-08-31 | 2023-08-31 | 2023-08-31 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER TBARU | [7 empty] | 14 | TRUE
466 | 2023-08-21 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 1 | SWITCHGEAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01212 | MEDAN NIAGA TASIK DAMAI 4 | TX PANEL | HOTSPOT | CABLE COMPARTMENT | PANEL 43045: TX 2 1000kVA - FUSE COMPARTMENT | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-27 | 2023-09-27 | CABLE END TO END | REPLACEMENT | Action Taken - Kerja Preventive Maintenance suisgear RMU SF6 Indkom 2+2 - Kerja Preventive Maintenance TX Hermatically Sealed 1000KVA - Kerja penukaran cable HT TX defect CBM - 12x term cable XLPE 70MMP - Tutup lubang cable menggunakan fibre plate dan silkcon - Maintenance EFI Emg 2nos - Check amps, voltage dan phase rotation - Normalise | [7 empty] | 37 | TRUE
467 | 2023-08-21 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 12 | TRANSFORMER | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01212 | MEDAN NIAGA TASIK DAMAI 4 | TX1 | HOTSPOT | TX CABLE | TX 1: HV-SIDE - RED & BLUE PHASE CABLE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-27 | 2023-09-27 | CABLE END TO END | REPLACEMENT | Action Taken - Kerja Preventive Maintenance suisgear RMU SF6 Indkom 2+2 - Kerja Preventive Maintenance TX Hermatically Sealed 1000KVA - Kerja penukaran cable HT TX defect CBM - 12x term cable XLPE 70MMP - Tutup lubang cable menggunakan fibre plate dan silkcon - Maintenance EFI Emg 2nos - Check amps, voltage dan phase rotation - Normalise | [7 empty] | 37 | TRUE
468 | 2023-08-21 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 29 | TRANSFORMER | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01212 | MEDAN NIAGA TASIK DAMAI 4 | TX2 | HOTSPOT | TX CABLE | TX 2: HV-SIDE - RED & BLUE PHASE CABLE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-27 | 2023-09-27 | CABLE END TO END | REPLACEMENT | Action Taken - Kerja Preventive Maintenance suisgear RMU SF6 Indkom 2+2 - Kerja Preventive Maintenance TX Hermatically Sealed 1000KVA - Kerja penukaran cable HT TX defect CBM - 12x term cable XLPE 70MMP - Tutup lubang cable menggunakan fibre plate dan silkcon - Maintenance EFI Emg 2nos - Check amps, voltage dan phase rotation - Normalise | [7 empty] | 37 | TRUE
469 | 2023-08-23 | EET ENGINEERING SERVICES | ULTRASOUND | 10 |  | TRANSFORMER | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J00681 | JLN PUJ 2/11 TMN PUNCAK JALIL | TX1 | CORONA DISCHARGE | TX CABLE | TX 1: HV-SIDE - RED PHASE CABLE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-10 | 2023-09-10 | TERMINATION | REPLACEMENT | [8 empty] | 18 | TRUE
470 | 2023-08-23 | EET ENGINEERING SERVICES | ULTRASOUND | 6 |  | TRANSFORMER | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J00681 | JLN PUJ 2/11 TMN PUNCAK JALIL | TX2 | CORONA DISCHARGE | TX CABLE | TX 2: HV-SIDE - RED PHASE CABLE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-10 | 2023-09-10 | TERMINATION | REPLACEMENT | [8 empty] | 18 | TRUE
471 | 2023-08-23 | TENBEX ENERGY | THERMOGRAPHY |  | 6 | TRANSFORMER | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00936 | JLN PUJ 2/29 TMN PUNCAK JALIL | TX1 | HOTSPOT | TX BUSHING | HT BUSHING YELLOW PHASE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-03 | 2023-09-03 | TX HV BUSHING | TIGHTNESS INSPECTION | [8 empty] | 11 | TRUE
472 | 2023-08-23 | TENBEX ENERGY | ULTRASOUND | 23 |  | SWITCHGEAR | RMU SF6 | FALCON BETA | SGB | XLPE | WKLS/PCE/J01188 | PST BDR PUNCAK JALIL F23B JLN PUJ 3/1 | 11KV CABLE FEEDER | ARCHING SOUND | CABLE COMPARTMENT | ARCHING SOUND CABLE BOX PANEL 40808 | REPAIR IMMEDIATELY | CABLE MAINTENANCE | 2023-10-30 | 2023-09-09 | 2023-09-09 | TERMINATION | NEW TERMINATION | Details : Termination guna heat shrink, crossing dan ada colour tape. Suis gear RMU Falcon Beta, saiz kabel 240mmp xlpe. Buat termination baru. Kerja siap dan normalised. | [7 empty] | 17 | TRUE
473 | 2023-08-24 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 3 | LVDB / F.PILLAR | VCB | TAMCO | E PUTRE | PILC | WKLS/PCE/J00814 | DESA TUN RAZAK NO. 8 | OUTGOING 6 | HOTSPOT | CABLE LUG / TERMINATION | LV BOARD (TX1): RED PHASE CABLE LUG CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-09 | 2023-09-09 | 2023-09-09 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
474 | 2023-08-24 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 34 | LVDB / F.PILLAR | VCB | TAMCO | E PUTRE | PILC | WKLS/PCE/J00814 | DESA TUN RAZAK NO. 8 | OUTGOING 6 | HOTSPOT | CABLE LUG / TERMINATION | LV BOARD (TX1): YELLOW PHASE CABLE LUG CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-09 | 2023-09-09 | 2023-09-09 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
475 | 2023-08-24 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 15 | LVDB / F.PILLAR | VCB | TAMCO | E PUTRE | PILC | WKLS/PCE/J00814 | DESA TUN RAZAK NO. 8 | OUTGOING 6 | HOTSPOT | FUSE / LINK | LV BOARD (TX2): RED PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-09 | 2023-09-09 | 2023-09-09 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
476 | 2023-08-24 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 48 | LVDB / F.PILLAR | VCB | TAMCO | E PUTRE | PILC | WKLS/PCE/J00814 | DESA TUN RAZAK NO. 8 | OUTGOING 6 | HOTSPOT | FUSE / LINK | LV BOARD (TX2): YELLOW PHASE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-09 | 2023-09-09 | 2023-09-09 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
477 | 2023-08-24 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 2 | TRANSFORMER | VCB | LKH HSS | MTM | PILC | WKLS/PCE/J00380 | PLAZA TOL WEST BOUND | TX1 | HOTSPOT | TX CABLE | TX 1: HV-SIDE - RED, YELLOW & BLUE PHASE CABLE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-23 | 2023-09-23 | TERMINATION | REPLACEMENT | [8 empty] | 30 | TRUE
478 | 2023-08-24 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | XLPE | WKLS/PCE/J00328 | TAM LAM HENG | OUTGOING 4 | HOTSPOT | FUSE / LINK | F/PILLAR (TX1): OUTGOING F4 - RED PHASE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-08 | 2023-09-08 | 2023-09-08 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 15 | TRUE
479 | 2023-08-24 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 29 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | XLPE | WKLS/PCE/J00328 | TAM LAM HENG | OUTGOING 4 | HOTSPOT | FUSE / LINK | F/PILLAR (TX1): OUTGOING F4 - BLUE PHASE PRIMARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-08 | 2023-09-08 | 2023-09-08 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 15 | TRUE
480 | 2023-08-24 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | 31 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | PILC | WKLS/PCE/J00328 | TAM LAM HENG | OUTGOING 6 | HOTSPOT | FUSE / LINK | F/PILLAR (TX1): OUTGOING F6 - RED PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-08 | 2023-09-08 | 2023-09-08 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 15 | TRUE
481 | 2023-08-24 | EET ENGINEERING SERVICES | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TOSHIBA | MTM | PILC | WKLS/PCE/J00328 | TAM LAM HENG | OUTGOING 2 | HOTSPOT | FUSE / LINK | LV BOARD (TX2): OUTGOING F2 - BLUE PHASE SECONDARY FUSE LINK CONNECTION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-08 | 2023-09-08 | 2023-09-08 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 15 | TRUE
482 | 2023-08-25 | TENBEX ENERGY | ULTRASOUND | 9 |  | SWITCHGEAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01177 | PST BDR PUNCAK JALIL F21C JLN PUJ 3/11 | 11KV CABLE FEEDER | TRACKING SOUND | CABLE COMPARTMENT | TRACKING SOUND CABLE BOX PANEL 40772 | REPAIR IMMEDIATELY | CABLE MAINTENANCE | 2023-10-30 | 2023-09-16 | 2023-09-16 | TERMINATION | NEW TERMINATION | Detail :suis gear rmu falcon beta.saiz kabel 240 xlpe .term heat shrink.term dalam keadaan cross.. tindakan buang pasir riseup(terhad) kabel dan buat term baru..tutup semula dan simen trenching.kerja siap dan normalised. | [7 empty] | 22 | TRUE
483 | 2023-08-26 | EET ENGINEERING SERVICES | ULTRASOUND | 8 |  | SWITCHGEAR | RMU SF6 | F&G INDKOM | MTM |  | WKLS/PCE/J00841 | DESA TUN RAZAK NO. 4 | 11KV CABLE FEEDER | CORONA DISCHARGE | CABLE COMPARTMENT | PANEL 10940: TX 1 - FUSE COMPARTMENT | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-26 | 2023-09-26 | FUSE / LINK | CLEANING | Action Taken - Potong telinga fuse holder fuse compartment tx - Lap dan ketatkan holder fuse compartment - Check amps, voltage dan phase rotation - Normalise | [7 empty] | 31 | TRUE
484 | 2023-08-26 | TENBEX ENERGY | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | ITEM | EWT | XLPE | WKLS/PCE/J01039 | PANDAN PERDANA NO. 1 | OUTGOING 2 | HOTSPOT | FUSE / LINK | CARRIER LINK YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-21 | 2023-09-21 | 2023-09-21 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 26 | TRUE
485 | 2023-08-27 | TENBEX ENERGY | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00716 | SEK MEN SAINS CHERAS | INCOMING 1 | HOTSPOT | FUSE / LINK | CARRIER LINK YELLOW PHASE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-05 | 2023-09-05 | FUSE / LINK | TIGHTNESS INSPECTION | [8 empty] | 9 | TRUE
486 | 2023-08-29 | TENBEX ENERGY | ULTRASOUND | 4 |  | SWITCHGEAR | VCB | UNIVAC | MTM | XLPE | WKLS/PCE/J00157 | TMN SEGAR FASA 2/2 | 11KV CABLE FEEDER | CORONA DISCHARGE | BREAKER COMPARTMENT | CORONA DISCHARGE BREAKER COMP. PANEL 30987 | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-10-17 | 2023-10-17 | BREAKER | SERVICING (CB ONLY) | Action Taken - Servis breaker yang defect cbm - Ketatkan skru dalam breaker - Letak minyak pada mekanikal breaker - Normalise | [7 empty] | 49 | TRUE
487 | 2023-08-29 | TENBEX ENERGY | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | ORMAZABAL | MTM | XLPE | WKLS/PCE/J00037 | TMN BAHAGIA | OUTGOING 2 | HOTSPOT | FUSE / LINK | CARRIER LINK YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-23 | 2023-09-23 | 2023-09-23 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 25 | TRUE
488 | 2023-09-05 | AKYZ ENGINEERING | THERMOGRAPHY |  | 50 | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J01079 | TMN SEGAR NO. 4 | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-23 | 2023-09-23 | 2023-09-23 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 18 | TRUE
489 | 2023-09-05 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | HHE | PILC | WKLS/PCE/J01070 | TMN GEMILANG | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-23 | 2023-09-23 | 2023-09-23 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 18 | TRUE
490 | 2023-09-06 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01052 | PANTAI CHERAS MEDICAL CENTRE | OUTGOING 6 | HOTSPOT | FUSE / LINK | HOTSPOT AT BLUE PHASE FUSE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-24 | 2023-09-24 | 2023-09-24 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 18 | TRUE
491 | 2023-09-06 | AKYZ ENGINEERING | THERMOGRAPHY |  | 2 | SWITCHGEAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01064 | TMN CHERAS NO. 1 | TX PANEL | HOTSPOT | CABLE COMPARTMENT | HOTSPOT AT PANEL 3265 - TX2 | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-29 | 2023-09-29 | FUSE / LINK | CLEANING | Action Taken - Lap dan ketatkan holder fuse compartment - Gosok dan ketatkan skru link holder lvdb - Check amps, voltage dan phase rotation - Normalise | [7 empty] | 23 | TRUE
492 | 2023-09-06 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01064 | TMN CHERAS NO. 1 | INCOMING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT BLUE PHASE LINK SCREW | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-29 | 2023-09-29 | FUSE / LINK | CLEANING | Action Taken - Lap dan ketatkan holder fuse compartment - Gosok dan ketatkan skru link holder lvdb - Check amps, voltage dan phase rotation - Normalise | [7 empty] | 23 | TRUE
493 | 2023-09-06 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01064 | TMN CHERAS NO. 1 | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-24 | 2023-09-24 | 2023-09-24 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 18 | TRUE
494 | 2023-09-06 | AKYZ ENGINEERING | THERMOGRAPHY |  | 50 | LVDB / F.PILLAR | RMU SF6 | SCHNEIDER | MTM | XLPE | WKLS/PCE/J01068 | TMN DESA AMAN NO. 1 | OUTGOING 6 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F6 BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-24 | 2023-09-24 | 2023-09-24 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 18 | TRUE
495 | 2023-09-07 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | EWT | XLPE | WKLS/PCE/J01101 | TMN SUPREME NO. 1 | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F8 BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-24 | 2023-09-24 | 2023-09-24 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 17 | TRUE
496 | 2023-09-08 | TENBEX ENERGY | ULTRASOUND | 14 |  | SWITCHGEAR | RMU SF6 | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00483 | LIAN YIT | TX PANEL | TRACKING SOUND | CABLE COMPARTMENT | TRACKING SOUND CABLE COMPARTMENT PANEL 4160 | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-10-13 | 2023-10-13 | RMU | TIGHTNESS INSPECTION | [8 empty] | 35 | TRUE
497 | 2023-09-08 | AKYZ ENGINEERING | ULTRASOUND | 11 |  | SWITCHGEAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01107 | TAMAN RAJAWALI | TX PANEL | ARCHING SOUND | CABLE COMPARTMENT | ARCING SOUND AT PANEL 8029 - TX2 1000KVA | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-10-11 | 2023-10-11 | RMU | TIGHTNESS INSPECTION | [8 empty] | 33 | TRUE
498 | 2023-09-08 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01107 | TAMAN RAJAWALI | OUTGOING 6 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F6 YELLOW PHASE CABLE TERMINATION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-24 | 2023-09-24 | 2023-09-24 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
499 | 2023-09-08 | AKYZ ENGINEERING | THERMOGRAPHY |  | 38 | LVDB / F.PILLAR | RMU SF6 | LUCY | EWT | PILC | WKLS/PCE/J01065 | TMN CHERAS NO. 2 | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F4 RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-24 | 2023-09-24 | 2023-09-24 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
500 | 2023-09-08 | AKYZ ENGINEERING | THERMOGRAPHY |  | 37 | LVDB / F.PILLAR | RMU SF6 | LUCY | EWT | PILC | WKLS/PCE/J01065 | TMN CHERAS NO. 2 | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F4 BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-24 | 2023-09-24 | 2023-09-24 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 16 | TRUE
501 | 2023-09-08 | AKYZ ENGINEERING | THERMOGRAPHY |  | 19 | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J01018 | TMN CHERAS UTAMA ( CHERAS BARU) | OUTGOING 6 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F6 RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-26 | 2023-09-26 | 2023-09-26 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 18 | TRUE
502 | 2023-09-08 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J01018 | TMN CHERAS UTAMA ( CHERAS BARU) | OUTGOING 6 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F6 BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-26 | 2023-09-26 | 2023-09-26 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 18 | TRUE
503 | 2023-09-11 | TENBEX ENERGY | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | EWT | XLPE | WKLS/PCE/J00484 | WAH LEONG SG BESI | OUTGOING 6 | HOTSPOT | FUSE / LINK | CARRIER LINK RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-30 | 2023-09-30 | 2023-09-30 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 19 | TRUE
504 | 2023-09-11 | TENBEX ENERGY | ULTRASOUND | 5 |  | SWITCHGEAR | RMU SF6 | F&G INDKOM | KILOSKAR | XLPE | WKLS/PCE/J00543 | CHOO KWAN GODOWN | TX PANEL | TRACKING SOUND | CABLE COMPARTMENT | TRACKING SOUND CABLE COMPARTMENT PANEL 7570 | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-29 | 2023-09-29 | FUSE / LINK | CLEANING | Action Taken - Potong telinga fuse holder fuse compartment tx - Lap dan ketatkan holder fuse compartment - Check amps, voltage dan phase rotation - Normalise | [7 empty] | 18 | TRUE
505 | 2023-09-12 | TENBEX ENERGY | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | E PUTRE | XLPE | WKLS/PCE/J00409 | DESA PETALING NO. 6 | OUTGOING 2 | HOTSPOT | FUSE / LINK | CARRIER LINK RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-30 | 2023-09-30 | 2023-09-30 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 18 | TRUE
506 | 2023-09-13 | AKYZ ENGINEERING | THERMOGRAPHY |  | 30 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J01012 | CHERAS BARU NO. 3 | OUTGOING 3 | HOTSPOT | CABLE LUG / TERMINATION | HOTSPOT AT OUTGOING F3 YELLOW PHASE CABLE TERMINATION | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-09-24 | 2023-09-30 | 2023-09-24 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 11 | TRUE
507 | 2023-09-15 | AKYZ ENGINEERING | THERMOGRAPHY |  | 2 | SWITCHGEAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01106 | TMN PERTAMA | TX PANEL | HOTSPOT | CABLE COMPARTMENT | HOTSPOT AT PANEL 6254 - TX1 1000KVA | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-30 | 2023-10-11 | RMU | TIGHTNESS INSPECTION | [8 empty] | 26 | TRUE
508 | 2023-09-15 | AKYZ ENGINEERING | THERMOGRAPHY |  | 2 | SWITCHGEAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01106 | TMN PERTAMA | TX PANEL | HOTSPOT | CABLE COMPARTMENT | HOTSPOT AT PANEL 6255 - TX2 1000KVA | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-30 | 2023-10-11 | RMU | TIGHTNESS INSPECTION | [8 empty] | 26 | TRUE
509 | 2023-09-15 | AKYZ ENGINEERING | THERMOGRAPHY |  | 19 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01106 | TMN PERTAMA | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F2 RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-30 | 2023-09-30 | 2023-09-30 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 15 | TRUE
510 | 2023-09-15 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01106 | TMN PERTAMA | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F2 YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-30 | 2023-09-30 | 2023-09-30 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 15 | TRUE
511 | 2023-09-15 | AKYZ ENGINEERING | THERMOGRAPHY |  | 23 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01106 | TMN PERTAMA | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F4 RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-30 | 2023-09-30 | 2023-09-30 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 15 | TRUE
512 | 2023-09-19 | AKYZ ENGINEERING | THERMOGRAPHY |  | 31 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01042 | PANDAN PERDANA NO. 4 | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F2 YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-30 | 2023-09-30 | 2023-09-30 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 11 | TRUE
513 | 2023-09-19 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | LKH HSS | MTM | XLPE | WKLS/PCE/J01048 | PANDAN PERDANA NO. 10 | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F5 YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-30 | 2023-09-30 | 2023-09-30 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 11 | TRUE
514 | 2023-09-19 | TENBEX ENERGY | THERMOGRAPHY |  | 1 | SWITCHGEAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00228 | TMN CONNAUGHT NO. 7 | TX PANEL | HOTSPOT | FUSE / LINK | HOTSPOT AT FUSE COMPARTMENT PANEL 13248 | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-30 | 2023-10-21 | FUSE / LINK | CLEANING | Action Taken - Potong telinga fuse holder fuse compartment tx - Lap dan ketatkan holder fuse compartment - Check amps, voltage dan phase rotation - Normalise | [7 empty] | 32 | TRUE
515 | 2023-09-20 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00001 | TMN TEKNOLOGI MALAYSIA | OUTGOING 6 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F6 YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-10-02 | 2023-09-30 | 2023-10-02 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 12 | TRUE
516 | 2023-09-20 | AKYZ ENGINEERING | THERMOGRAPHY |  | 42 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00001 | TMN TEKNOLOGI MALAYSIA | OUTGOING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F1 BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-10-02 | 2023-09-30 | 2023-10-02 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 12 | TRUE
517 | 2023-09-21 | AKYZ ENGINEERING | THERMOGRAPHY |  | 17 | LVDB / F.PILLAR | RMU SF6 | EPE | MTM | XLPE | WKLS/PCE/J01047 | PANDAN PERDANA NO. 9 | OUTGOING 3 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F3 BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-30 | 2023-09-30 | 2023-09-30 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
518 | 2023-09-21 | AKYZ ENGINEERING | THERMOGRAPHY |  | 39 | LVDB / F.PILLAR | RMU SF6 | EPE | MTM | XLPE | WKLS/PCE/J01044 | PANDAN PERDANA NO. 6 | OUTGOING 5 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F5 YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-30 | 2023-09-30 | 2023-09-30 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
519 | 2023-09-21 | AKYZ ENGINEERING | THERMOGRAPHY |  | 42 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | ASEA LEPPER | XLPE | WKLS/PCE/J01089 | TMN SHAMELIN PERKASA NO. 10 | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F4 RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-30 | 2023-09-30 | 2023-09-30 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
520 | 2023-09-21 | AKYZ ENGINEERING | THERMOGRAPHY |  | 30 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | ASEA LEPPER | XLPE | WKLS/PCE/J01089 | TMN SHAMELIN PERKASA NO. 10 | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F8 BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-06-30 | 2023-09-30 | 2023-09-30 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 9 | TRUE
521 | 2023-09-21 | AKYZ ENGINEERING | THERMOGRAPHY |  | 38 | TRANSFORMER | RMU SF6 | F&G INDKOM | ASEA LEPPER | XLPE | WKLS/PCE/J01087 | TMN SHAMELIN PERKASA NO. 8 | TX2 | HOTSPOT | EARTHING | HOTSPOT AT TX2 EARTHING CABLE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-10-20 | 2023-10-20 | EARTHING | TIGHTNESS INSPECTION | Action Taken - Pasang dan ketatkan Link carrier LVDB incoming TX1 & TX2 - neutral phase - Ketatkan cable earthing tx1 & tx2 - Normalise | [7 empty] | 29 | TRUE
522 | 2023-09-22 | TENBEX ENERGY | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00252 | DESA TUN RAZAK E | OUTGOING 3 | HOTSPOT | FUSE / LINK | FUSE LINK RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-10-02 | 2023-10-02 | 2023-10-02 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 10 | TRUE
523 | 2023-09-22 | TENBEX ENERGY | THERMOGRAPHY |  | >=D3052 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00252 | DESA TUN RAZAK E | OUTGOING 5 | HOTSPOT | FUSE / LINK | FUSE LINK YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-10-02 | 2023-10-02 | 2023-10-02 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 10 | TRUE
524 | 2023-09-22 | TENBEX ENERGY | THERMOGRAPHY |  | >=D3053 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00252 | DESA TUN RAZAK E | OUTGOING 7 | HOTSPOT | FUSE / LINK | FUSE LINK RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-10-02 | 2023-10-02 | 2023-10-02 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 10 | TRUE
525 | 2023-09-22 | TENBEX ENERGY | THERMOGRAPHY |  | >=D3054 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00252 | DESA TUN RAZAK E | OUTGOING 7 | HOTSPOT | FUSE / LINK | FUSE LINK YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-10-02 | 2023-10-02 | 2023-10-02 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 10 | TRUE
526 | 2023-09-22 | TENBEX ENERGY | ULTRASOUND | 31 |  | SWITCHGEAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00062 | JLN 118C NO. 2 DESA TUN RAZAK | TX PANEL | ARCHING SOUND | CABLE COMPARTMENT | ARCHING SOUND CABLE COMPARTMENT PANEL 7570 | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-09-26 | 2023-09-26 | RMU | TIGHTNESS INSPECTION | [8 empty] | 4 | TRUE
527 | 2023-09-22 | TENBEX ENERGY | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00062 | JLN 118C NO. 2 DESA TUN RAZAK | INCOMING 2 | HOTSPOT | FUSE / LINK | FUSE LINK RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-10-02 | 2023-10-02 | 2023-10-02 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 10 | TRUE
528 | 2023-09-22 | TENBEX ENERGY | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J00062 | JLN 118C NO. 2 DESA TUN RAZAK | INCOMING 2 | HOTSPOT | FUSE / LINK | FUSE LINK BLUE PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-10-02 | 2023-10-02 | 2023-10-02 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 10 | TRUE
529 | 2023-09-25 | AKYZ ENGINEERING | THERMOGRAPHY |  | 10 | TRANSFORMER | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J01105 | TMN MUDA NO. 5 | TX1 | HOTSPOT | EARTHING | HOTSPOT AT TX1 EARTHING CABLE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-10-17 | 2023-10-17 | LUG | CLEANING | Action Taken - Gosong dan ketatkan cable lug earthing cable TX1 - LV Side - Gosok dan ketatkan bolt dan nut link carrier incoming 1 F/Pillar TX2 - Tambah link carrier incoming 2 di F/Pillar TX2 - Normalise | [7 empty] | 22 | TRUE
530 | 2023-09-25 | AKYZ ENGINEERING | ULTRASOUND | 8 |  | SWITCHGEAR | VCB | TAMCO | EWT | XLPE | WKLS/PCE/J01071 | TMN KENCANA NO. 1 | 11KV CABLE FEEDER | TRACKING SOUND | CABLE COMPARTMENT | TRACKING SOUND AT PANEL 7882 - TX1 1000KVA | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-11-08 | 2023-11-08 | TERMINATION | REPLACEMENT | [8 empty] | 44 | TRUE
531 | 2023-09-25 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TAMCO | EWT | XLPE | WKLS/PCE/J01071 | TMN KENCANA NO. 1 | OUTGOING 6 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F6 BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-10-02 | 2023-10-02 | 2023-10-02 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 7 | TRUE
532 | 2023-09-25 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J01013 | CHERAS BARU NO. 4 | OUTGOING 7 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F6 RED PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-10-02 | 2023-10-02 | 2023-10-02 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 7 | TRUE
533 | 2023-09-25 | TENBEX ENERGY | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | FALCON BETA | MTM | XLPE | WKLS/PCE/J01221 | PANTAI AVENUE | OUTGOING 4 | HOTSPOT | FUSE / LINK | FUSE LINK YELLOW PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 2023-10-02 | 2023-10-02 | 2023-10-02 | FUSE / LINK | REPLACEMENT | TUKAR FIUS DAN HOLDER BARU | [7 empty] | 7 | TRUE
534 | 2023-09-27 | TENBEX ENERGY | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | RMU SF6 | LUCY | MTM | XLPE | WKLS/PCE/J00162 | KEM PEMADAM | OUTGOING 1 | HOTSPOT | FUSE / LINK | CARRIER LINK BLUE PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 28/10/23 | 28/10/23 | 2023-10-28 | FUSE / LINK | REPLACEMENT | TUKAR FIUS HOLDER BARU | [7 empty] | 31 | TRUE
535 | 2023-09-29 | AKYZ ENGINEERING | THERMOGRAPHY |  | 50 | LVDB / F.PILLAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01165 | NO. 1 PUSAT PERDAGANGAN KUCHAI | OUTGOING 2 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F2 YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 28/10/23 | 28/10/23 | 2023-10-28 | FUSE / LINK | REPLACEMENT | TUKAR FIUS HOLDER BARU | [7 empty] | 29 | TRUE
536 | 2023-09-29 | AKYZ ENGINEERING | THERMOGRAPHY |  | 1 | SWITCHGEAR | RMU SF6 | F&G INDKOM | MTM | XLPE | WKLS/PCE/J01205 | NO. 3 PST PERDAGANGAN JLN KUCHAI MAJU 13 | 11KV CABLE FEEDER | HOTSPOT | CABLE COMPARTMENT | HOTSPOT AT PANEL PANEL 43607 – TX3 | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-11-16 | 2023-11-16 | RMU | NONE | defect berulang | [7 empty] | 48 | TRUE
537 | 2023-10-05 | AKYZ ENGINEERING | THERMOGRAPHY |  | 50 | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00637 | JLN PUJ 9/21 TMN PUNCAK JALIL | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F8 BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 28/10/23 | 28/10/23 | 2023-10-28 | FUSE / LINK | REPLACEMENT | TUKAR FIUS HOLDER BARU | [7 empty] | 23 | TRUE
538 | 2023-10-09 | AKYZ ENGINEERING | ULTRASOUND | 6 |  | SWITCHGEAR | VCB | EPE |  |  | WKLS/PCE/J01512 | SSU 11KV TAMAN PUNCAK JALIL | 11KV CABLE FEEDER | TRACKING SOUND | BREAKER COMPARTMENT | TRACKING SOUND AT PANEL 49836- BUSTIE | REPAIR IMMEDIATELY | SUBSTATION MAINTENANCE |  | 2023-11-15 | 2023-11-15 | BREAKER | SERVICING (CB ONLY) | [8 empty] | 37 | TRUE
539 | 2023-10-10 | AKYZ ENGINEERING | THERMOGRAPHY |  | 45 | LVDB / F.PILLAR | RMU SF6 | EPE | MTM | XLPE | WKLS/PCE/J00033 | BALAI BOMBA JLN PINTAS PUCHONG | OUTGOING 4 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F4 BLUE PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 28/10/23 | 28/10/23 | 2023-10-28 | FUSE / LINK | REPLACEMENT | TUKAR FIUS HOLDER BARU | [7 empty] | 18 | TRUE
540 | 2023-10-10 | TENBEX ENERGY | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | EPE | MTM | XLPE | WKLS/PCE/J00221 | RMH RAKYAT PETALING | OUTGOING 1 | HOTSPOT | FUSE / LINK | CARRIER LINK RED PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 28/10/23 | 28/10/23 | 2023-10-28 | FUSE / LINK | REPLACEMENT | TUKAR FIUS HOLDER BARU | [7 empty] | 18 | TRUE
541 | 2023-10-16 | TENBEX ENERGY | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | TAMCO | MTM | XLPE | WKLS/PCE/J00054 | SEK REN DESA PETALING JLN 2/125 | OUTGOING 2 | HOTSPOT | FUSE / LINK | CARRIER LINK BLUE PHASE | REPAIR IMMEDIATELY | LV MAINTENANCE | 28/10/23 | 28/10/23 | 2023-10-28 | FUSE / LINK | REPLACEMENT | TUKAR FIUS HOLDER BARU | [7 empty] | 12 | TRUE
542 | 2023-10-24 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | EPE | MTM |  | WKLS/PCE/J00970 | NO. 2 RMH/KEDAI JLN RADIN ANUM SRI PETAL | OUTGOING 7 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F7 YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 28/10/23 | 28/10/23 | 2023-10-28 | FUSE / LINK | REPLACEMENT | TUKAR FIUS HOLDER BARU | [7 empty] | 4 | TRUE
543 | 2023-10-24 | AKYZ ENGINEERING | THERMOGRAPHY |  | >=D3051 | LVDB / F.PILLAR | VCB | EPE | MTM |  | WKLS/PCE/J00970 | NO. 2 RMH/KEDAI JLN RADIN ANUM SRI PETAL | OUTGOING 8 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F8 YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 28/10/23 | 28/10/23 | 2023-10-28 | FUSE / LINK | REPLACEMENT | TUKAR FIUS HOLDER BARU | [7 empty] | 4 | TRUE
544 | 2023-10-26 | AKYZ ENGINEERING | THERMOGRAPHY |  | 42 | LVDB / F.PILLAR | RMU SF6 | TAMCO | MTM | XLPE | WKLS/PCE/J00815 | DESA TUN RAZAK NO. 7 | OUTGOING 1 | HOTSPOT | FUSE / LINK | HOTSPOT AT OUTGOING F1 YELLOW PHASE FUSE LINK | REPAIR IMMEDIATELY | LV MAINTENANCE | 28/10/23 | 28/10/23 | 2023-10-28 | FUSE / LINK | REPLACEMENT | TUKAR FIUS HOLDER BARU | [7 empty] | 2 | TRUE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE